## Overview
Analysis to support the paper: Energy saving potential of high temperature heat pumps in the UK food and drink sector (2018) by Samuel J G Cooper, Geoffrey P Hammond, Neil Hewitt, Jonathan B Norman, Savvas A Tassou, Walid Youssef
presented at 2nd International Conference on Sustainable Energy and Resource Use in Food Chains, ICSEF 2018. Paphos Cyprus, 17-19 October 2018.
corresponding author: Samuel JG Cooper |  | sjgcooper@bath.edu
Contents
Dairy totals | Takes the energy efficiency improvements that could be made in each process (through HTHPS) and applies this to whole of dairy sector
Food and Drink totals | Extrapolates energy efficiency improvements to UK Food and Drink sector
Heat Pumps | Details the nominal performance of heat pumps used as basis of calculations
Milk | Detailed calculations for efficiency improvements in Liquid milk processing through HTHPs
Cheese | Detailed calculations for efficiency improvements in Cheese processing through HTHPs
Yogurt | Detailed calculations for efficiency improvements in Yogurt processing through HTHPs
Powder | Considerations regarding potential efficiency improvements in Milk Powder production
Cleaning in Place | Detailed calculations for efficiency improvements in water heating for Cleaning in Place (CIP) through HTHPs
Climate | Climate data and bins used for calculations
References | References to data sources used in calculations
Constants used in calculations
Latent heat vaporisation of water (kJ / kg) | 2257
Specific heat water (kJ / kg K) | 4.19
Specific heat steam (kJ / kg K) | 2.02
Density of milk (kg / m3) | 1020
Specific heat milk (kJ / kg K) | 3.95

## Dairy totals
Savings across the UK Dairy industry
1. Calculating the relative proportion of heating / steam used in the modelled processes.
Several sources give quite varied estimates of the specific energy demand, so all are presented
Specific energy demand [kWh/kg]
| Proportion of raw milk demand [1] | Proportion of dairy products [1] |  | Total relative to products [2] | Heat relative to raw milk [3] | Total relative to raw milk [4] | Heat relative to products [5]
Liquid Milk | 48% | 82% |  | 0.30556 | 0.165 | 0.175 | 0.36 |  | 0.14667 | 0.0792 | 0.084 | 0.2952
Cheese | 31% | 6% |  | 1.1944 | 0.46 | 0.412 | 3.6 |  | 0.37028 | 0.1426 | 0.12772 | 0.216
Yogurt | 3% | 4% |  | 0.30556 | 0.295 | 0.2 | 0.72 |  | 0.0091667 | 0.00885 | 0.006 | 0.0288
Powder | 8% | 1% |  | 3.0833 | 0.585 | 0.5 | 14.4 |  | 0.24667 | 0.0468 | 0.04 | 0.144
Other | 10% | 7% |  | 0.69444 | 0.295 | 0.2 | 3.24 |  | 0.069444 | 0.0295 | 0.02 | 0.2268
[9 empty] | 0.84222 | 0.30695 | 0.27772 | 0.9108
Relative proportion of process heating
Liquid Milk | 17.41% | 25.8% | 30.25% | 32.41%
Cheese | 43.96% | 46.46% | 45.99% | 23.72%
Yogurt | 1.088% | 2.883% | 2.16% | 3.162%
Powder | 29.29% | 15.25% | 14.4% | 15.81%
Other | 8.245% | 9.611% | 7.201% | 24.9%
2. Use these proportions to determine the relative change in energy input for heating / steam generation.
| Efficiency |  |  |  | Energy input to each process if HTHPs were used, relative to current energy input
| Current (excluding boiler inefficiency) | Direct replacement | Optimized |  | Direct replacement | Optimized
Liquid Milk | 85.87% | 187.4% | 261.6% |  | 45.81% | 32.83%
Cheese | 92.16% | 195.5% | 611.1% |  | 47.15% | 15.08%
Yogurt | 81.58% | 187.4% | 228.5% |  | 43.52% | 35.71%
Powder | 85.73% | 295% | 321.3% |  | 29.06% | 26.68%
Other | 85.87% | 187.4% | 261.6% |  | 45.81% | 32.83%
HTHP direct replacement |  |  |  |  | HTHP Optimized
7.978% | 11.82% | 13.86% | 14.85% |  | 5.717% | 8.471% | 9.929% | 10.64%
20.73% | 21.9% | 21.68% | 11.18% |  | 6.63% | 7.006% | 6.935% | 3.576%
0.4737% | 1.255% | 0.9403% | 1.376% |  | 0.3887% | 1.03% | 0.7715% | 1.129%
8.511% | 4.431% | 4.185% | 4.594% |  | 7.815% | 4.069% | 3.843% | 4.219%
3.777% | 4.403% | 3.299% | 11.41% |  | 2.707% | 3.155% | 2.364% | 8.175%
41.47% | 43.81% | 43.96% | 43.41% |  | 23.26% | 23.73% | 23.84% | 27.74%
|  |  |  | Difference: | 18.21% | 20.08% | 20.12% | 15.67%
With HTHP direct replacement, average energy input for heat / steam generation is: |  |  |  |  | 43.16% | of current energy input
With HTHP optimized, average energy input for heat / steam generation is: |  |  |  |  | 24.64% | of current energy input
For Cleaning In Place, direct replacement, the energy-use could be approximately |  |  |  |  | 33.59% | of current energy input
For Cleaning In Place, optimized, the energy-use could be approximately |  |  |  |  | 20.27% | of current energy input
Moving from direct replacement to optimized HTHP system, may reduce energy use for heat / steam generation by |  |  |  |  | 18.52% | of current energy input
3. Current GHG emissions and energy costs
Steam generation in UK dairy sector (from [6])
1369.3908 | TJ steam for processes
1338.3467 | TJ steam for CIP
Currently generated using: |  |  | [8] |  | [8] |  | [9]
| Energy [6] | Energy | GHG intensities [8]: | Total GHG: | CO2 intensity | Total CO2: | Fuel prices [9]: | Fuel costs
Fuel | TJ | GWh | kt-CO2e/GWh | kt-CO2e | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000
Coal | 88.468 | 24.5744 | 0.32442 | 7.9724 | 0.32132 | 7.8962 | 7.7913 | 191.4668
Oil | 349.9417 | 97.206 | 0.26789 | 26.0407 | 0.24536 | 23.8509 | 42.2706 | 4108.9561
Gas | 3220.6951 | 894.6375 | 0.18416 | 164.76 | 0.18381 | 164.4416 | 22.4767 | 20108.5365
Total | 3659.1048 | 1016.418 |  | 198.7731 |  | 196.1887 |  | 24408.9594
4. GHG emissions and electricity costs if HTHPs used
| Energy use |  |  |  | [8] |  | [8] |  | [9]
| Processes | CIP | Total | Total | GHG intensity [8]: | Total GHG: | CO2 intensity | Total CO2: | Electricity price | Total cost:
| TJ | TJ | TJ | GWh | kt-CO2e/GWh | kt-CO2e | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000
HTHP Direct replacement | 591.0824 | 449.5447 | 1040.6271 | 289.0631 | 0.35156 | 101.623 | 0.18398 | 53.1831 | 102.32 | 29576.9345
HTHP Optimized | 337.455 | 271.2523 | 608.7072 | 169.0853 | 0.35156 | 59.4436 | 0.18398 | 31.1091 | 102.32 | 17300.8126
Improved case | 306.7773 | 246.593 | 553.3702 | 153.714 | 0.35156 | 54.0397 | 0.18398 | 28.281 | 102.32 | 15728.0115
10%
where the improved case is a 10% average improvement in HTHP nominal COPs over current performance
| GHG Saving: | CO2 Saving | Cost saving:
| kt-CO2e | kt-CO2 | £'000
HTHP Direct replacement | 97.1501 | 143.0056 | -5167.9752
HTHP Optimized | 139.3295 | 165.0797 | 7108.1467
Improved case | 144.7335 | 167.9078 | 8680.9479
5. Comparison based on projections to 2035
Just taking "Average" and "Best Case" energy savings.
Note that BEIS projections only detail CO2 for future electricity generation (not GHG) and so the basis for both has been modified slightly.
Year | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
CO2 Emissions (current heating) | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887 | 196.1887
Power station CO2 emissions [9] | 102.911 | 65.8787 | 60.1609 | 57.9282 | 54.3215 | 48.2825 | 44.3051 | 35.5917 | 33.5065 | 33.2832 | 31.5969 | 26.0638 | 28.5495 | 26.936 | 24.8274 | 27.5606 | 25.6684 | 21.7899 | 21.3978 | 19.6309 | 17.2392
Electricity generation (TWh) [9] | 322.423 | 324.1244 | 326.9893 | 327.6848 | 324.0964 | 315.8363 | 308.8231 | 292.3422 | 282.3446 | 270.7703 | 272.4901 | 279.6926 | 283.8693 | 293.4225 | 304.0267 | 306.0128 | 312.3151 | 327.3302 | 335.3346 | 346.5725 | 367.7195
Electricity CO2 intensity | 0.31918 | 0.20325 | 0.18398 | 0.17678 | 0.16761 | 0.15287 | 0.14346 | 0.12175 | 0.11867 | 0.12292 | 0.11596 | 0.093187 | 0.10057 | 0.091799 | 0.081662 | 0.090064 | 0.082188 | 0.066568 | 0.06381 | 0.056643 | 0.046881
CO2 Emissions (HTHP direct replacement) | 92.2632 | 58.7524 | 53.1831 | 51.1007 | 48.4496 | 44.1897 | 41.4702 | 35.1925 | 34.3038 | 35.5317 | 33.5186 | 26.9371 | 29.0718 | 26.5358 | 23.6054 | 26.0341 | 23.7574 | 19.2425 | 18.4452 | 16.3734 | 13.5517
CO2 Emissions (HTHP optimized) | 53.9687 | 34.3668 | 31.1091 | 29.891 | 28.3403 | 25.8484 | 24.2577 | 20.5856 | 20.0658 | 20.784 | 19.6065 | 15.7566 | 17.0054 | 15.5219 | 13.8078 | 15.2284 | 13.8967 | 11.2558 | 10.7894 | 9.5775 | 7.9269
CO2 Emissions (HTHP improved) | 49.0624 | 31.2426 | 28.281 | 27.1736 | 25.7639 | 23.4986 | 22.0525 | 18.7142 | 18.2416 | 18.8946 | 17.8241 | 14.3242 | 15.4594 | 14.1109 | 12.5526 | 13.844 | 12.6334 | 10.2325 | 9.8085 | 8.7068 | 7.2063
Coal price ($/ton coal) [9] | 58.0106 | 57.0066 | 73 | 65 | 65 | 65 | 67 | 70 | 72 | 74 | 77 | 79 | 81 | 84 | 86 | 88 | 88 | 88 | 88 | 88 | 88
$/£ [9] | 1.5286 | 1.3542 | 1.2493 | 1.2621 | 1.278 | 1.2955 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313 | 1.313
Coal price (£'000/GWh) | 5.06 | 5.6128 | 7.7913 | 6.8669 | 6.7814 | 6.6898 | 6.8036 | 7.1082 | 7.3113 | 7.5144 | 7.819 | 8.0221 | 8.2252 | 8.5299 | 8.733 | 8.936 | 8.936 | 8.936 | 8.936 | 8.936 | 8.936
Oil price (p/kWh) [9] | 4.2317 | 3.8418 | 4.2271 | 4.1513 | 4.244 | 4.3253 | 4.4026 | 4.5692 | 4.6823 | 4.7948 | 4.96 | 5.0727 | 5.1854 | 5.2982 | 5.4635 | 5.5764 | 5.5844 | 5.5924 | 5.6005 | 5.6086 | 5.6168
Oil price (£'000/GWh) | 42.3166 | 38.4183 | 42.2706 | 41.5134 | 42.4398 | 43.253 | 44.0263 | 45.6917 | 46.8227 | 47.9485 | 49.5997 | 50.7265 | 51.8539 | 52.9818 | 54.6351 | 55.764 | 55.8438 | 55.9242 | 56.0051 | 56.0865 | 56.1685
Gas price (p/kWh) [9] | 2.1542 | 1.7502 | 2.2477 | 2.2205 | 2.2907 | 2.351 | 2.5098 | 2.6224 | 2.7301 | 2.873 | 3.0675 | 3.1889 | 3.2709 | 3.3529 | 3.4743 | 3.5564 | 3.5564 | 3.5564 | 3.5564 | 3.5564 | 3.5564
Gas price (£'000/GWh) | 21.5421 | 17.5021 | 22.4767 | 22.2045 | 22.9071 | 23.5097 | 25.0981 | 26.2239 | 27.3005 | 28.7297 | 30.6755 | 31.889 | 32.709 | 33.5292 | 34.7435 | 35.5642 | 35.5642 | 35.5642 | 35.5642 | 35.5642 | 35.5642
Fuel cost (current heating) | 23510.1741 | 19530.4225 | 24408.9594 | 24069.1219 | 24785.6053 | 25401.5486 | 26900.5106 | 28077.0787 | 29155.1982 | 30548.2289 | 32456.9487 | 33657.1838 | 34505.3637 | 35356.2892 | 36608.2943 | 37457.2296 | 37464.9857 | 37472.7948 | 37480.6574 | 37488.5738 | 37496.5443
Electricity price (p/kWh) [9] | 9.8818 | 9.8314 | 10.2318 | 10.6758 | 11.3627 | 11.7249 | 12.029 | 11.9893 | 12.1085 | 12.3757 | 13.0943 | 13.1365 | 12.8155 | 12.7955 | 12.7989 | 12.9654 | 13.0283 | 12.503 | 12.4874 | 12.5143 | 11.3913
Electricity price (£'000/GWh) | 98.8181 | 98.3144 | 102.3183 | 106.7579 | 113.6267 | 117.2485 | 120.2904 | 119.8935 | 121.085 | 123.7573 | 130.9432 | 131.365 | 128.1554 | 127.9553 | 127.9886 | 129.654 | 130.2826 | 125.0296 | 124.8735 | 125.1426 | 113.9127
Electricity cost (HTHP direct replacement) | 28564.6708 | 28419.0753 | 29576.4441 | 30859.78 | 32845.2826 | 33892.215 | 34771.502 | 34656.781 | 35001.1908 | 35773.6526 | 37850.8571 | 37972.7594 | 37044.9966 | 36987.1486 | 36996.7742 | 37478.1972 | 37659.8868 | 36141.4339 | 36096.3228 | 36174.1201 | 32927.9634
Electricity cost (HTHP optimized) | 16708.6963 | 16623.5313 | 17300.5258 | 18051.2038 | 19212.6091 | 19825.0045 | 20339.3371 | 20272.2318 | 20473.6919 | 20925.5378 | 22140.5835 | 22211.8893 | 21669.2012 | 21635.3635 | 21640.9939 | 21922.5987 | 22028.8767 | 21140.6688 | 21114.2814 | 21159.7883 | 19260.9726
Electricity cost (HTHP improved) | 15189.7239 | 15112.3012 | 15727.7507 | 16410.1852 | 17466.0083 | 18022.7314 | 18490.3064 | 18429.3017 | 18612.4471 | 19023.2162 | 20127.8031 | 20192.6266 | 19699.2738 | 19668.5122 | 19673.6308 | 19929.6352 | 20026.2516 | 19218.7898 | 19194.8012 | 19236.1712 | 17509.9751

## Food and Drink totals
Extrapolating savings from Dairy to entire Food & Drink sector
The calculated savings are extrapolated in order to provide an estimate across the whole food & drink sector
1. HTHP COPs that could be achieved for steam generation
Without further information, pasteurization option 1 is assumed to be required when the requirement is for steam, drying option 1 is assumed to be required when the requirement is for drying.
This is a conservative approach.
| Steam (general) | Drying
Effective COP | 187.4% | 232%
Electricity requirement: | 45.81% | 36.95% | of the original heat input from the steam
2. Summary of current GHG emissions and energy costs
Energy mix for steam generation relates to UK in 2010 [6]
Meat subsector used:
4850 | TJ steam |  | Boiler efficiency: | 74.06%
Currently generated using: |  |  | [8] | 2017 | [8] | 2017 | [9] | 2017 | [8] | 2030 | [9] | 2030
| Energy [6] | Energy | GHG intensities [8]: | Total GHG: | CO2 intensity | Total CO2: | Fuel prices [9]: | Fuel costs | CO2 intensity | Total CO2: | Fuel prices [9]: | Fuel costs
Fuel | TJ | GWh | kt-CO2e/GWh | kt-CO2e | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000 | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000
Oil | 1117.4746 | 310.4096 | 0.26789 | 83.1562 | 0.24536 | 76.1634 | 42.2706 | 13121.1964 | 0.24536 | 76.1634 | 55.764 | 17309.6947
Gas | 5430.9265 | 1508.5907 | 0.18416 | 277.8281 | 0.18381 | 277.2912 | 22.4767 | 33908.2034 | 0.18381 | 277.2912 | 35.5642 | 53651.7573
Total | 6548.4011 | 1819.0003 |  | 360.9842 |  | 353.4546 |  | 47029.3998 |  | 353.4546 |  | 70961.452
Other food & drink subsectors used:
29585.4674 | TJ steam (general) |  | Boiler efficiency: | 74%
5755.932 | TJ steam (drying)
Currently generated using: |  |  | [8] | 2017 | [8] | 2017 | [9] | 2017 | [8] | 2030 | [9] | 2030
| Energy [6] | Energy | GHG intensities [8]: | Total GHG: | CO2 intensity | Total CO2: | Fuel prices [9]: | Fuel costs | CO2 intensity | Total CO2: | Fuel prices [9]: | Fuel costs
Fuel | TJ | GWh | kt-CO2e/GWh | kt-CO2e | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000 | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000
Coal | 760.4911 | 211.2475 | 0.32442 | 68.5329 | 0.32132 | 67.8779 | 7.7913 | 1645.8925 | 0.32132 | 67.8779 | 8.936 | 1887.7176
Oil | 4414.4952 | 1226.2487 | 0.26789 | 328.5019 | 0.24536 | 300.8776 | 42.2706 | 51834.2506 | 0.24536 | 300.8776 | 55.764 | 68380.5824
Gas | 42583.6617 | 11828.7949 | 0.18416 | 2178.4381 | 0.18381 | 2174.2281 | 22.4767 | 265872.7659 | 0.18381 | 2174.2281 | 35.5642 | 420681.1238
Total | 47758.6479 | 13266.2911 |  | 2575.4728 |  | 2542.9835 |  | 319352.9089 |  | 2542.9835 |  | 490949.4237
3. Comparison to impacts of electricity
|  |  | [8] | 2017 | [8] | 2017 | [9] | 2017 | [8] | 2030 | [9] | 2030
| Energy use |  | GHG intensity [8]: | Total GHG: | CO2 intensity | Total CO2: | Electricity price | Total cost: | CO2 intensity | Total CO2: | Electricity price | Total cost:
| TJ | GWh | kt-CO2e/GWh | kt-CO2e | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000 | kt-CO2/GWh | kt-CO2 | £'000/GWh | £'000
Conservative | 17902.889 | 4973.0247 | 0.35156 | 1748.3166 | 0.18398 | 914.9591 | 102.32 | 508839.889 | 0.090064 | 447.8886 | 102.32 | 508839.889
10% performance improvement | 16275.3536 | 4520.9316 | 0.35156 | 1589.3787 | 0.18398 | 831.781 | 102.32 | 462581.7173 | 0.090064 | 407.1715 | 102.32 | 462581.7173
10%
where the improved case is a 10% average improvement in HTHP nominal COPs over current performance
4. Savings
Absolute: |  | 2017 | 2017 | 2030 | 2030
| GHG Saving: | CO2 Saving | Cost saving: | CO2 Saving | Cost saving:
| kt-CO2e | kt-CO2 | £'000 | kt-CO2 | £'000
Conservative | 1285.2907 | 2124.4847 | -147625.5555 | 2618.7042 | 53050.0191
10% performance improvement | 1491.8119 | 2232.5649 | -87518.4607 | 2671.6113 | 116856.7528
Proportional: |  | 2017 | 2017 | 2030 | 2030
| GHG Saving: | CO2 Saving | Cost saving: | CO2 Saving | Cost saving:
Conservative | 41% | 68.7% | -37.78% | 84.68% | 8.851%
10% performance improvement | 47.58% | 72.19% | -22.4% | 86.39% | 19.5%

## Heat Pumps
Heat pump models used as basis for calculations
|  | Source temp | Heat supply lower temperature (if range) | Heat supply higher temp
| COP | T0 | T1 | T2 | Exergy efficiency | Reference
Kobelco steam grow | 3.2 | 65 |  | 120 | 44.78% | [10]
| 2.5 | 70 |  | 165 | 54.22% | [10]
Viking Heat Engine | 2.5 | 80 |  | 140 | 36.32% | [11]
| 3.1 | 60 |  | 110 | 40.47% | [11]
SGH120 | 3.5 | 65 |  | 120 | 48.98% | [10]
SGH165 | 2.5 | 70 |  | 165 | 54.22% | [10]
NeatPump | 3.05 | 8 | 60 | 90 | 58.57% | [12] | N.B. different equation for exergy efficiency is to integrate heat supply over temperature range
Heliotherm HP | 5.5 | 10 |  | 35 | 44.64% | [13]
Heat pump exergy efficiencies - based on actual units listed above
CIP heat pumps | 58.57% | i.e. mid temperature, providing it over a temperature range
Preheat heat pumps | 44.64% | i.e. low temperature, providing heating for culture stages
Pasteurisation heat pumps | 44.73% | i.e. higher temperature for the top part of pasteurisation cycles
Steam replacement heat pumps | 54.22% | i.e very high temperatures for direct steam replacemet

## Milk
Liquid Milk Pasteurization
Heat in temperature (°C) | 144
Heat out temperature (°C) | 139
Condensate tank temp (°C) | 50
Current efficiency (excluding boiler / combustion)
Efficiency of phase change process is: | 85.87%
Option 1 heat pump
Heat in temperature (°C) | 144
Heat out temperature (°C) | 142
Efficiency of heat transfer | 100% | Here we are assuming that the heat pump is coupled directly to the HX (i.e. the working fluid is circulated at this temperature)
Source temp above ambient (°C) | 10 | i.e. the refrigeration condenser.
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 165.9% | -3 | 1.685% | 0.010161
COP at temp bin 2 | 172.9% | 2.5 | 11.12% | 0.064361
COP at temp bin 3 | 179.7% | 7.5 | 24.4% | 0.13575
COP at temp bin 4 | 187.2% | 12.5 | 25.51% | 0.13629
COP at temp bin 5 | 195.3% | 17.5 | 22.27% | 0.11401
COP at temp bin 6 | 204.1% | 22.5 | 12.52% | 0.06133
COP at temp bin 7 | 215.1% | 28.15 | 2.491% | 0.011577
Weighted average COP | 187.4%
Option 2 heat pump
Heat in temperature (°C) | 82 | i.e. If heat is supplied to the HX at a lower temperature
Heat out temperature (°C) | 78 | Note: 2 - 3°C difference between HX and milk (more causes issues at plates) [14]
Efficiency of heat transfer | 95%
Source temp above ambient (°C) | 10
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 216.3% | -3 | 1.685% | 0.0077925
COP at temp bin 2 | 233.9% | 2.5 | 11.12% | 0.047563
COP at temp bin 3 | 252.6% | 7.5 | 24.4% | 0.096591
COP at temp bin 4 | 274.6% | 12.5 | 25.51% | 0.092915
COP at temp bin 5 | 300.7% | 17.5 | 22.27% | 0.074042
COP at temp bin 6 | 332.4% | 22.5 | 12.52% | 0.037666
COP at temp bin 7 | 377.3% | 28.15 | 2.491% | 0.006602
Weighted average COP | 261.6%

## Cheese
Cheese - Pasteurization stage only
Heat in temperature (°C) | 95
Heat out temperature (°C) | 78
Milk in temperature (°C) | 4
Milk out temperature (°C) | 34
HTST temperature (°C) | 72
Current efficiency
Efficiency of heat transfer | 98% | Assuming all single phase heating without return
Efficiency of regeneration | 95% | [14]
Temp at end of preheat | 40.1
Temp at end of preheat if perfect | 42
Effective efficiency (taking account of regenerator inefficiency | 92.16% | i.e. relative to efficiency if we had a perfect preheat system.
Could understand as HX_efficiency * net heat input to milk / heat actually supplied, i.e. B10 * (B6-B5)/(B7-B12)
For cheese and yogurt, one of the HX systems outputs milk at a higher temperature than it enters. The second HP option for these processes assumes that two heat pump stages are used - one to supply the additional low temperature heat and one to take the milk from the outlet of the regenerator up to the maximum temperature that is required.
Option 1 heat pump
Heat in temperature (°C) | 95
Heat out temperature (°C) | 83
Efficiency of heat transfer | 98% | Here we are assuming that the heat pump is coupled directly to the HX (i.e. the working fluid is circulated at this temperature)
Source temp above ambient (°C) | 0 | There doesn't seem to be a suitable refrigeration cycle to take heat from
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 176% | -3 | 1.685% | 0.0095765
COP at temp bin 2 | 187.2% | 2.5 | 11.12% | 0.059435
COP at temp bin 3 | 198.7% | 7.5 | 24.4% | 0.12282
COP at temp bin 4 | 211.6% | 12.5 | 25.51% | 0.12054
COP at temp bin 5 | 226.4% | 17.5 | 22.27% | 0.098331
COP at temp bin 6 | 243.5% | 22.5 | 12.52% | 0.051422
COP at temp bin 7 | 266.1% | 28.15 | 2.491% | 0.0093606
Weighted average COP | 207.9%
Effective COP taking account of regenerator inefficiency | 195.5%
Option 2 heat pump
Two heat pumps: low temp to 29°C followed by regenerative preheat and then heat pump supplying top up heat at higher temp
i.e. as the milk leaves the pasteuriser HX at a higher temperature than it enters, the regenerator can't supply as great a proportion of the total heat required. The heat pumps therefore need to supply a greater proportion. It is better to provide this additional heat at the low temperature end of the process than the high temperature end.
Efficiency of regeneration | 95%
Temperature differential | 5 | i.e. across the HX between incoming milk and outgoing milk
Milk temp exiting low temp heat pump | 29
Temp after regenerator | 65.1 | i.e. cooling the milk from 72°C to 34°C increases the temp of the incoming milk from 29°C to 65.1°C
Low temp heat pump | This stage takes milk from 4°C to 29°C
Temperature differential | 5 | i.e. between milk and heating fluid
Heat in temperature (°C) | 34 | i.e. fluid temp entering HX to warm milk
Heat out temperature (°C) | 9
Efficiency of heat transfer | 98%
Source temp above ambient (°C) | 0
As part of the temperature of the heat demand is sometimes lower than the ambient temperature, the temperature requirement will be the part above ambient.
| COP | Temp bin centre | Proportion of time at temperature |  | Average temp that heat is supplied at | Proportion of heating supplied by heat pump
COP at temp bin 1 | 536.6% | -3 | 1.685% | 0.0031406 | 21.5 | 1
COP at temp bin 2 | 692% | 2.5 | 11.12% | 0.016077 | 21.5 | 1
COP at temp bin 3 | 939.1% | 7.5 | 24.4% | 0.025983 | 21.5 | 1
COP at temp bin 4 | 1431% | 12.5 | 25.51% | 0.017834 | 23.25 | 0.86
COP at temp bin 5 | 2449% | 17.5 | 22.27% | 0.0090905 | 25.75 | 0.66
COP at temp bin 6 | 5085% | 22.5 | 12.52% | 0.0024623 | 28.25 | 0.46
COP at temp bin 7 | 19833% | 28.15 | 2.491% | 0.00012558 | 31.075 | 0.234
Weighted average COP for low temp supply | 1312%
High temp heat pump | This stage takes milk from the outlet of the regenerator (65.1) up to max temperature required (72)
Heat in temperature (°C) | 82
Heat out temperature (°C) | 78 | Note: 2 - 3°C difference between HX and milk (more causes issues at plates) [14]
Efficiency of heat transfer | 98%
Source temp above ambient (°C) | 0 | There doesn't seem to be a suitable refrigeration cycle to take heat from
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 190.2% | -3 | 1.685% | 0.00886
COP at temp bin 2 | 203.7% | 2.5 | 11.12% | 0.054609
COP at temp bin 3 | 217.8% | 7.5 | 24.4% | 0.11205
COP at temp bin 4 | 233.9% | 12.5 | 25.51% | 0.10907
COP at temp bin 5 | 252.6% | 17.5 | 22.27% | 0.088145
COP at temp bin 6 | 274.6% | 22.5 | 12.52% | 0.045596
COP at temp bin 7 | 304.5% | 28.15 | 2.491% | 0.0081795
Weighted average COP for high temp supply | 229.8%
Weighted average COP for both heat pumps | 649.8% | i.e. (heat supplied by LTHP + heat supplied by HTHP) / (electrical input into LTHP + electrical input into HTHP)
Effective COP taking account of regenerator inefficiency | 611.1% | i.e. COP * heat input to milk / heat supplied by heat pumps

## Yogurt
Yogurt | Pasteurisation & Other processes
Heat in temperature (°C) | 144
Heat out temperature (°C) | 139
Condensate tank temp (°C) | 50
Milk in temperature (°C) | 4
Second stage milk out temperature (°C) | 40
Second stage max temp temperature (°C) | 93
Pasteurization temp | 72
Current efficiency
Efficiency of phase change process is: | 85.87%
Efficiency of regeneration | 95%
Total efficiency of present heating: | 81.58%
Option 1 heat pump
As per liquid milk pasteurisation stage
Averaged COP | 187.4%
Option 2 heat pump
1st and 3rd heat supply processes operate as per liquid milk pasteurisation. 2nd process operates 2-stage heat pump as per cheese production
1st process average COP | 261.6%
3rd process average COP | 261.6%
Two heat pumps used for second process: low temp to 29°C followed by regenerative preheat and then heat pump supplying top up heat at higher temp
i.e. as the milk leaves the pasteuriser HX at a higher temperature than it enters, the regenerator can't supply as great a proportion of the total heat required. The heat pumps therefore need to supply a greater proportion. It is better to provide this additional heat at the low temperature end of the process than the high temperature end.
Efficiency of regeneration | 95%
Temperature differential | 5 | i.e. across the HX between incoming milk and outgoing milk
Milk temp exiting low temp heat pump | 35
Temp after regenerator | 85.35 | i.e. cooling the milk from 93°C to 40°C increases the temp of the incoming milk from 35°C to 85.35°C
Low temp heat pump | This stage takes milk from 4°C to 35°C
Temperature differential | 5 | i.e. between milk and heating fluid
Heat in temperature (°C) | 40
Heat out temperature (°C) | 9
Efficiency of heat transfer | 98%
Source temp above ambient (°C) | 0
As part of the temperature of the heat demand is sometimes lower than the ambient temperature, the temperature requirement will be the part above ambient.
| COP | Temp bin centre | Proportion of time at temperature |  | Average temp that heat is supplied at | Proportion of heating supplied by heat pump
COP at temp bin 1 | 483% | -3 | 1.685% | 0.0034897 | 24.5 | 1
COP at temp bin 2 | 603.7% | 2.5 | 11.12% | 0.018428 | 24.5 | 1
COP at temp bin 3 | 781.3% | 7.5 | 24.4% | 0.031232 | 24.5 | 1
COP at temp bin 4 | 1095% | 12.5 | 25.51% | 0.023294 | 26.25 | 0.8871
COP at temp bin 5 | 1650% | 17.5 | 22.27% | 0.013497 | 28.75 | 0.72581
COP at temp bin 6 | 2750% | 22.5 | 12.52% | 0.004553 | 31.25 | 0.56452
COP at temp bin 7 | 6053% | 28.15 | 2.491% | 0.00041149 | 34.075 | 0.38226
Weighted average COP for low temp supply | 1033%
High temp heat pump | This stage takes milk from the outlet of the regenerator (85.35) up to max temperature required (93)
Heat in temperature (°C) | 98
Heat out temperature (°C) | 96
Efficiency of heat transfer | 98%
Source temp above ambient (°C) | 0 | There doesn't seem to be a suitable refrigeration cycle to take heat from
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 165.5% | -3 | 1.685% | 0.010184
COP at temp bin 2 | 175.1% | 2.5 | 11.12% | 0.063528
COP at temp bin 3 | 184.9% | 7.5 | 24.4% | 0.13196
COP at temp bin 4 | 195.8% | 12.5 | 25.51% | 0.13027
COP at temp bin 5 | 208.2% | 17.5 | 22.27% | 0.10697
COP at temp bin 6 | 222.1% | 22.5 | 12.52% | 0.056362
COP at temp bin 7 | 240.4% | 28.15 | 2.491% | 0.010362
Weighted average COP for stage 2 | 192.3%
Weighed average COP of both heat pumps | 5.5369 | i.e. (heat supplied by LTHP + heat supplied by HTHP) / (electrical input into LTHP + electrical input into HTHP)
Effective COP taking account of regenerator inefficiency | 224% | i.e. COP * heat input to milk / heat supplied by heat pumps
Putting the three heating processes together
Approx proportion of heat input supplied by 2nd heat pump: | 86.34%
Pasteurisation 1 | 3.4
Culture 2 | 40.45
Pasteurisation & Homogenisation 3 | 3 | where 83 and 23 are the temperature range of the processes
Averaged COP | 228.5%
i.e. this is the harmonic average of the three heat processes - with the middle process being the one with the two-stage heat pump analysed above.

## Powder
Milk Powder
There are three major heat-consuming processes in addition to CIP (which is similar to other processes).
The first stage is Pasteurization. This is essentially the same as for cheese
The second stage is vacuum evaporation. This removes around half the moisture content.
The final stage is a spray dryer to remove the final moisture content.
The potential energy efficiency of each can be evaluated and then the weighted total found.
Heat in temperature (°C) | 144
Heat out temperature (°C) | 140
Condensate tank temp (°C) | 50
Pasteurization
Current efficiency (excluding boiler / combustion)
Efficiency of phase change process is: | 85.73%
Heat Pump
Efficiency of Pasteurization (option 1) | 195.5%
Efficiency of Pasteurization (option 2) | 611.1%
Heat Pump for vacuum evaporator
Current efficiency
Efficiency of heat transfer | 98% | (excluding boiler)
Heat pump
Heat in temperature (°C) | 70
Heat out temperature (°C) | 40
Efficiency of heat transfer | 95%
Source temp above ambient (°C) | 0 | i.e. as we're not sure there is additional heat available from the refrigerant cycle
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 332.3% | -3 | 1.685% | 0.0050718
COP at temp bin 2 | 367.3% | 2.5 | 11.12% | 0.030292
COP at temp bin 3 | 406.1% | 7.5 | 24.4% | 0.060083
COP at temp bin 4 | 454.1% | 12.5 | 25.51% | 0.056178
COP at temp bin 5 | 515.1% | 17.5 | 22.27% | 0.04323
COP at temp bin 6 | 594.9% | 22.5 | 12.52% | 0.021046
COP at temp bin 7 | 721.1% | 28.15 | 2.491% | 0.0034539
Weighted average COP | 433.1%
Heat Pump for spray dryer
Current efficiency (excluding boiler / combustion)
Efficiency of phase change process is: | 85.73%
The reduction in temperature required to extract latent heat depends upon the actual conditions (temperature, pressure and relative humidity of mixture entering the condenser).
Estimating it at | 15
So heat available at | 45
And needs to be supplied at | 142
Possible COP (option 1) | 232%
Could be supplied at | 135
Possible COP (option 2) | 245.8%
Combined efficiencies
[2] indicates that the pasteurization stage consumes 2.5% of energy while evaporation uses 45% and drying 51%.
However, total energy use data ([1], [6]) indicates that it will be much higher - probably 10%, using 5% for this analysis
Pasteurization | 5.076%
Evaporation | 45.69%
Drying | 51.78%
Current efficiency | 91.2% |  | i.e. sum of heat inputs / sum of energy inputs
HTHP option 1 | 295%
HTHP option 2 | 321.3%

## Cleaning in Place
Cleaning in Place
Current efficiency
Efficiency of heat transfer | 98% | (excluding boiler)
HTHP direct replacement - i.e. HTHP supplies heat at same temperature as boiler (all at max temp)
Temperature glide across condenser | 10
CIP temperature | 80
HX differential | 5
Heat in temperature (°C) | 85
Heat out temperature (°C) | 75
Efficiency of heat transfer | 95%
Source temp above ambient (°C) | 0 | i.e. as we're not sure there is additional heat available from the refrigerant cycle
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 249.1% | -3 | 1.685% | 0.0067645
COP at temp bin 2 | 266.8% | 2.5 | 11.12% | 0.041692
COP at temp bin 3 | 285.2% | 7.5 | 24.4% | 0.085542
COP at temp bin 4 | 306.4% | 12.5 | 25.51% | 0.083272
COP at temp bin 5 | 330.9% | 17.5 | 22.27% | 0.067291
COP at temp bin 6 | 359.7% | 22.5 | 12.52% | 0.034808
COP at temp bin 7 | 398.9% | 28.15 | 2.491% | 0.0062439
Weighted average COP | 291.8%
HTHP Optimized - i.e. temperature glide matches heat demand warming water from cold
Cold water in temperature | 12
CIP temperature | 80
HX differential | 5
Heat in temperature (°C) | 85
Heat out temperature (°C) | 17
Efficiency of heat transfer | 95%
Source temp above ambient (°C) | 0 | i.e. as we're not sure there is additional heat available from the refrigerant cycle
| COP | Temp bin centre | Proportion of time at temperature
COP at temp bin 1 | 358% | -3 | 1.685% | 0.0047073
COP at temp bin 2 | 399.7% | 2.5 | 11.12% | 0.027837
COP at temp bin 3 | 446.9% | 7.5 | 24.4% | 0.054601
COP at temp bin 4 | 506.8% | 12.5 | 25.51% | 0.050343
COP at temp bin 5 | 585.2% | 17.5 | 22.27% | 0.038049
COP at temp bin 6 | 692.4% | 22.5 | 12.52% | 0.018083
COP at temp bin 7 | 873% | 28.15 | 2.491% | 0.002853
Weighted average COP | 483.5%

## Climate
Climate data |  |  |  | Data from [7]
Used for binning average temperatures for heat pump heat sources
Hour of day | Heathrow air temp [°C] | Glasgow air temp [°C] | Leicester air temp [°C]
0 | -0.1 | -6 | -0.9 | Max temp: | 31.2
1 | -0.3 | -4 | -0.7 | Min temp: | -6
2 | -0.4 | -4.1 | -0.8 | Average temp: | 11.2929
3 | -0.7 | -4.2 | -0.9
4 | -0.7 | -4.3 | -0.9 | Start operation: | 6
5 | -1.2 | -4.5 | -0.8 | End operation | 17
6 | -1.8 | -4.4 | -0.7 | Annual operating hours: | 4015
7 | -0.9 | -4.4 | -0.4 | Average temp during operating hours | 13.6529 | 12.1159 | 12.067
8 | 0 | -4.4 | -0.8 | Average temp during operating hours | 12.6119
9 | -1.6 | -4.1 | -0.7
10 | -0.1 | -3.1 | -0.6 | Temp bin bottom | Temp bin top |  | Operating hours in that temp bin | Heathrow | Glasgow | Leicester | Total hours in that temp bin
11 | 0 | -1.5 | -0.5 | -6 | 0 |  | 67.6667 | 61 | 39 | 103 | 548
12 | 2.1 | 0.1 | -0.6 | 0 | 5 |  | 446.6667 | 372 | 469 | 499 | 3798
13 | 1.9 | 0.1 | -0.7 | 5 | 10 |  | 979.6667 | 842 | 1081 | 1016 | 7391
14 | 2.4 | 0.2 | -0.6 | 10 | 15 |  | 1024.3333 | 1024 | 1039 | 1010 | 6969
15 | 1.9 | 0.1 | -0.4 | 15 | 20 |  | 894 | 907 | 932 | 843 | 5021
16 | 2.2 | -0.5 | -0.6 | 20 | 25 |  | 502.6667 | 620 | 419 | 469 | 2163
17 | 1.7 | -1.7 | -0.8 | 25 | 31.3 |  | 100 | 189 | 36 | 75 | 390
18 | 0.4 | -2.3 | -0.6 |  |  |  | 4015 | 4015 | 4015 | 4015 | 8760
19 | 0.4 | -2.6 | -0.8
20 | -0.4 | -3 | -0.5
21 | 0.5 | -3.4 | -0.7
22 | -0.6 | -3.7 | -0.7
23 | 0.6 | -5.2 | -0.6
0 | 1.7 | -1.4 | -0.6 | Centre temp | Proportion of time at temperature
1 | 1.5 | 1.2 | -0.7 | -3 | 1.685% |  | -0.05056
2 | 1.8 | 1.1 | -0.4 | 2.5 | 11.12% |  | 0.27812
3 | 1.8 | 1 | -2 | 7.5 | 24.4% |  | 1.83
4 | 1.1 | 0.7 | -2.4 | 12.5 | 25.51% |  | 3.1891
5 | 1.3 | 0.6 | -3.1 | 17.5 | 22.27% |  | 3.8966
6 | 1.3 | 0.6 | -3.9 | 22.5 | 12.52% |  | 2.8169
7 | 1.9 | 0.7 | -3.3 | 28.15 | 2.491% |  | 0.70112
8 | 2.5 | 0.6 | -2.7
9 | 3.5 | 1 | -2.5 |  |  | Weighted average temperature | 12.6614
10 | 3.4 | 2.3 | -0.6 |  |  | Error due to binning: | 0.049431
11 | 5.9 | 4.5 | 1.8
12 | 6.1 | 6.6 | 3
13 | 6.2 | 6.5 | 3.1
14 | 6 | 6.6 | 2.9
15 | 5.8 | 6.2 | 3.2
16 | 6.1 | 5.8 | 3.1
17 | 5.4 | 4.2 | 1
18 | 4.3 | 3.3 | 0.4
19 | 3.9 | 3 | -0.3
20 | 2.9 | 2.5 | -0.9
21 | 3.1 | 2 | -1.3
22 | 2.6 | 1.6 | -1.8
23 | 2.4 | -0.4 | -0.8
0 | 2.2 | -0.5 | 0.2
1 | 2.1 | 1.3 | 1.1
2 | 1.4 | 1.2 | 1.7
3 | 0.6 | 1.1 | 1.4
4 | 0.7 | 1 | 0.6
5 | 0.8 | 0.8 | 0.7
6 | 2.9 | 0.9 | 1.6
7 | 2 | 0.9 | 1.8
8 | 2.2 | 0.9 | 0.7
9 | 1.5 | 1.1 | -0.5
10 | 2.4 | 2.1 | 2
11 | 3.4 | 3.6 | 4.4
12 | 4.4 | 5.1 | 5.2
13 | 4.7 | 4.9 | 5.2
14 | 4.2 | 5.1 | 5.3
15 | 4.3 | 5.2 | 5.2
16 | 4.5 | 4.5 | 5.2
17 | 3.9 | 3.4 | 3.2
18 | 2.8 | 2.8 | 3.7
19 | 2.2 | 2.5 | 2.9
20 | 2.1 | 2.2 | 2.1
21 | 1.8 | 1.8 | 1.3
22 | 1.9 | 1.5 | 1.1
23 | 0.9 | 0.2 | 1.6
0 | -0.1 | -0.5 | 2.1
1 | 0.9 | 2.1 | 2.8
2 | 2 | 2 | 3.1
3 | 0.9 | 1.9 | 2.9
4 | 1.6 | 1.7 | 2.5
5 | 0.5 | 1.5 | 2.1
6 | 1.2 | 1.6 | 2.4
7 | 1.2 | 1.6 | 2.6
8 | 2.4 | 1.6 | 3.6
9 | 0.5 | 1.9 | 4.1
10 | 2.2 | 3.3 | 3.9
11 | 5 | 5.4 | 5.1
12 | 5 | 7.6 | 5.3
13 | 5.3 | 7.7 | 5.1
14 | 5.4 | 7.6 | 5.2
15 | 5.2 | 7.5 | 5.1
16 | 4.1 | 6.8 | 5.5
17 | 5 | 5.2 | 4.7
18 | 3.1 | 4.3 | 4.8
19 | 2.4 | 3.9 | 4.6
20 | 3 | 3.5 | 3.5
21 | 1.6 | 2.9 | 2.7
22 | 1.4 | 2.5 | 2.6
23 | 1.4 | 0.6 | 2.1
0 | 1.3 | 4.7 | 1.6
1 | 0.1 | 6.6 | -0.5
2 | -1.1 | 6.6 | -1.9
3 | -2.4 | 6.5 | -3.2
4 | -2.1 | 6.3 | -2.6
5 | -1.9 | 6.2 | -1.9
6 | -1.2 | 6.2 | -1.2
7 | -2.2 | 6.3 | -2.4
8 | -1.2 | 6.2 | -2.2
9 | -2.1 | 6.5 | -2.5
10 | -0.3 | 7.5 | 2.2
11 | 0.3 | 9 | 3.1
12 | 0 | 10.6 | 3.7
13 | 1.5 | 10.3 | 3.5
14 | 1.6 | 10.6 | 3.8
15 | 1.5 | 10.3 | 4
16 | 1.5 | 10 | 2.9
17 | -0.1 | 8.9 | 3.4
18 | 0 | 8.2 | 2.3
19 | -0.7 | 7.9 | 2
20 | -1.4 | 7.6 | -0.1
21 | -0.9 | 7.2 | -1.2
22 | -0.4 | 6.9 | -0.6
23 | -0.3 | 5.5 | -0.6
0 | -0.1 | 4.7 | -0.6
1 | 0.3 | 6.3 | 0.3
2 | -0.3 | 6.2 | 0.5
3 | -1 | 6.1 | 1.2
4 | -0.3 | 6 | 1.2
5 | 0.4 | 5.9 | 0.3
6 | 0.7 | 5.9 | -0.2
7 | 0.4 | 5.9 | -0.9
8 | -0.7 | 5.9 | 0.2
9 | 0.9 | 6.1 | 1.1
10 | 1.8 | 6.9 | 2.1
11 | 1.8 | 8.2 | 4.7
12 | 3 | 9.5 | 5.8
13 | 3 | 9.1 | 5.8
14 | 3.2 | 9.5 | 5.9
15 | 3.1 | 9.3 | 5.8
16 | 3.1 | 9 | 5.7
17 | 1.4 | 8.1 | 5.7
18 | 0.6 | 7.5 | 2.7
19 | 1.8 | 7.3 | 3.8
20 | 1.7 | 7.1 | 1.7
21 | 1.1 | 6.7 | 2.8
22 | -0.7 | 6.5 | 1.4
23 | -0.6 | 5.3 | 3.2
0 | -0.5 | 3.6 | 5
1 | -0.5 | 5.7 | 5.2
2 | -0.5 | 5.7 | 5.3
3 | 0.6 | 5.6 | 5.7
4 | -1.1 | 5.4 | 5.4
5 | 0 | 5.2 | 5
6 | -0.7 | 5.3 | 5.4
7 | -1 | 5.3 | 5.7
8 | -1.5 | 5.3 | 6.3
9 | 0.2 | 5.6 | 5.2
10 | 1.7 | 6.7 | 5.2
11 | 1 | 8.5 | 5.7
12 | 3.8 | 10.3 | 5.8
13 | 3.7 | 10.3 | 6.2
14 | 3.9 | 10.3 | 6.1
15 | 3.8 | 10.4 | 6.5
16 | 3.8 | 9.6 | 6
17 | 2.1 | 8.3 | 5.6
18 | 3.2 | 7.6 | 6.2
19 | 1.5 | 7.3 | 6.1
20 | 1 | 6.9 | 6.3
21 | 0.9 | 6.4 | 5.8
22 | 1 | 6.1 | 5.5
23 | 0.5 | 4.5 | 5
0 | 0 | 1.5 | 3
1 | -1.2 | 3.1 | 3.2
2 | -2.2 | 3.1 | 3.5
3 | -3.5 | 3 | 4.5
4 | -4.8 | 2.8 | 4.4
5 | -3.2 | 2.7 | 3.3
6 | -1.6 | 2.8 | 3.7
7 | -3.1 | 2.8 | 4.3
8 | -2.6 | 2.8 | 3.3
9 | -0.8 | 3 | 3.5
10 | -0.2 | 3.8 | 5.6
11 | 3.6 | 5.2 | 5.5
12 | 5.6 | 6.5 | 6.6
13 | 5.9 | 6.3 | 7
14 | 6 | 6.5 | 6.9
15 | 5.9 | 6.5 | 6.9
16 | 5.9 | 6 | 6.9
17 | 4 | 5 | 5.5
18 | 1.8 | 4.5 | 6.6
19 | 0.2 | 4.2 | 5.4
20 | 0 | 4 | 5.3
21 | 1.1 | 3.6 | 4.7
22 | -0.7 | 3.4 | 5.3
23 | -0.5 | 2.2 | 4.7
0 | -0.3 | 1.2 | 4.1
1 | 0.4 | 2.7 | 4
2 | 0.3 | 2.6 | 3.7
3 | -0.1 | 2.6 | 3.6
4 | -0.7 | 2.4 | 3.2
5 | -0.1 | 2.3 | 3.6
6 | 0.3 | 2.4 | 3.1
7 | 0.6 | 2.4 | 2.6
8 | 0.4 | 2.4 | 3.2
9 | 0.6 | 2.6 | 3.7
10 | 1.2 | 3.3 | 2.9
11 | 3.7 | 4.5 | 4.8
12 | 3.7 | 5.7 | 6.5
13 | 3.6 | 5.7 | 6.5
14 | 3.8 | 5.8 | 6.6
15 | 3.7 | 5.7 | 6.5
16 | 3.6 | 5.3 | 6.6
17 | 2.4 | 4.4 | 5.1
18 | 1.8 | 3.9 | 5.4
19 | 2.8 | 3.7 | 3.4
20 | 1.9 | 3.4 | 5.2
21 | 1.2 | 3.1 | 4.2
22 | 0 | 2.9 | 5.5
23 | 0 | 1.8 | 4.3
0 | 0.1 | -3.2 | 3.1
1 | -0.4 | -0.8 | 0.8
2 | -0.4 | -0.9 | -0.6
3 | -0.9 | -1 | -1.2
4 | -1.2 | -1.2 | -1.8
5 | -0.9 | -1.4 | -1
6 | -1.4 | -1.3 | -0.1
7 | -2.1 | -1.3 | -1.3
8 | -0.7 | -1.3 | -0.1
9 | 0.5 | -1 | -0.4
10 | 1.1 | 0.2 | 0.9
11 | 3.8 | 2.1 | 4.1
12 | 4.4 | 4 | 4.1
13 | 4.8 | 4 | 3.9
14 | 4.7 | 4.1 | 4.2
15 | 4.6 | 4.2 | 4.1
16 | 3.8 | 3.3 | 3.4
17 | 4.1 | 1.9 | 3.7
18 | 2.4 | 1.1 | 1.8
19 | 2.2 | 0.8 | 2
20 | 1.5 | 0.4 | 2.4
21 | -0.1 | -0.1 | -1
22 | 0.1 | -0.5 | -0.1
23 | 0.3 | -2.2 | -0.5
0 | 0.5 | -5.3 | -0.9
1 | -0.5 | -1.8 | -0.9
2 | -1.4 | -1.9 | -0.9
3 | -1.9 | -2.1 | 0.7
4 | -2.2 | -2.4 | -0.3
5 | -2.5 | -2.6 | -1.4
6 | -2.2 | -2.6 | -1
7 | -1.9 | -2.5 | -0.7
8 | -1.4 | -2.6 | -0.6
9 | -1.9 | -2.1 | 0.7
10 | 0 | -0.2 | 2.5
11 | 0.3 | 2.6 | 3.7
12 | 2 | 5.5 | 3.3
13 | 2.1 | 5.5 | 3.8
14 | 1.8 | 5.5 | 3.7
15 | 2 | 5.5 | 3.5
16 | 2.1 | 4.5 | 3.6
17 | 1.8 | 2.3 | 2.7
18 | 0.6 | 1.1 | 2.5
19 | -0.4 | 0.6 | 1.5
20 | -0.3 | 0 | 0.6
21 | -0.3 | -0.7 | 1.1
22 | -1.5 | -1.3 | 0.5
23 | -1.3 | -3.9 | 0
0 | -1 | -0.7 | -0.4
1 | -1.2 | 0.9 | -1.3
2 | -1.2 | 0.8 | -2.2
3 | -2.5 | 0.7 | -3.2
4 | -3.9 | 0.6 | -2.4
5 | -2.6 | 0.5 | -1.9
6 | -1.2 | 0.5 | -1.5
7 | -2.5 | 0.6 | -2.6
8 | -2.2 | 0.5 | -1.9
9 | -2.9 | 0.8 | -1.7
10 | -1.1 | 1.6 | -1.4
11 | 1.8 | 2.9 | 1.8
12 | 3.9 | 4.2 | 3.4
13 | 3.7 | 3.8 | 3.5
14 | 3.9 | 4.2 | 3.4
15 | 3.8 | 4 | 3.4
16 | 3.8 | 3.7 | 3.4
17 | 2.1 | 2.8 | 2.7
18 | 0.9 | 2.2 | 1
19 | 1.5 | 2 | 0.2
20 | 0.2 | 1.7 | 1.2
21 | 0.1 | 1.4 | 0.3
22 | -1.8 | 1.1 | -0.7
23 | 0.3 | -0.1 | -0.3
0 | 2.5 | 0.3 | 0
1 | 3.4 | 1.7 | 0.2
2 | 4.3 | 1.7 | 0.6
3 | 4.6 | 1.6 | 1.4
4 | 4.4 | 1.5 | -0.8
5 | 5.1 | 1.4 | -0.9
6 | 3.9 | 1.4 | -1.1
7 | 3.6 | 1.4 | -0.8
8 | 3.8 | 1.4 | -0.7
9 | 5.4 | 1.6 | 1
10 | 6.6 | 2.4 | 1.1
11 | 6.9 | 3.6 | 2.5
12 | 9.3 | 4.8 | 1.8
13 | 9.2 | 4.6 | 3.3
14 | 9.3 | 4.8 | 3
15 | 9.4 | 4.5 | 3.1
16 | 9.3 | 4.3 | 3.2
17 | 8 | 3.4 | 1.9
18 | 6.1 | 2.9 | 0.9
19 | 6.9 | 2.7 | 1
20 | 5.5 | 2.5 | 2.2
21 | 4.8 | 2.2 | 0.4
22 | 4.2 | 1.9 | 1.2
23 | 4.3 | 0.9 | 1.2
0 | 4.5 | 0.7 | 1.2
1 | 3.8 | 3.1 | 1.6
2 | 3.5 | 3 | 1.8
3 | 1.4 | 2.9 | 2.8
4 | 2.6 | 2.7 | 1.2
5 | 1.8 | 2.5 | 3.3
6 | 1.1 | 2.6 | 1.2
7 | 1.5 | 2.6 | 1.8
8 | 1.8 | 2.6 | 1
9 | 3.5 | 2.9 | 0.2
10 | 4.1 | 4.2 | 3.2
11 | 7.2 | 6.1 | 6.1
12 | 7.5 | 8.1 | 7.6
13 | 7.7 | 7.9 | 7.6
14 | 7.6 | 8.1 | 7.7
15 | 7.6 | 8 | 7.5
16 | 7 | 7.4 | 6.9
17 | 6.3 | 5.9 | 7.6
18 | 5.5 | 5.1 | 4.4
19 | 5.1 | 4.7 | 4.8
20 | 4.1 | 4.3 | 4.2
21 | 3.6 | 3.8 | 3.7
22 | 2.8 | 3.5 | 3.7
23 | 3.1 | 1.7 | 4.1
0 | 3.3 | 6.1 | 4.4
1 | 3.4 | 7 | 5
2 | 3.8 | 7 | 5.4
3 | 6.5 | 6.9 | 5
4 | 4.7 | 6.9 | 4.4
5 | 4.3 | 6.8 | 4.8
6 | 5 | 6.8 | 4.9
7 | 4.2 | 6.8 | 5.4
8 | 5.8 | 6.8 | 5.9
9 | 4.3 | 7 | 6.5
10 | 7.9 | 7.5 | 6.8
11 | 9.4 | 8.3 | 7.1
12 | 11.1 | 9.1 | 8.2
13 | 11.1 | 8.9 | 8.3
14 | 11.2 | 9.1 | 8.4
15 | 11.1 | 9.1 | 8.3
16 | 9.7 | 8.8 | 8.3
17 | 9.1 | 8.2 | 7.8
18 | 7.2 | 7.9 | 7.4
19 | 8.6 | 7.7 | 6.9
20 | 5.9 | 7.5 | 6.7
21 | 6.9 | 7.3 | 5.3
22 | 5.1 | 7.2 | 5.7
23 | 6 | 6.5 | 6
0 | 7 | 2.9 | 6.2
1 | 8.2 | 4.6 | 6.4
2 | 8.8 | 4.5 | 6.3
3 | 8.3 | 4.4 | 6.3
4 | 7.6 | 4.2 | 7
5 | 6.7 | 4 | 6.5
6 | 7.5 | 4.1 | 6
7 | 8.1 | 4.1 | 6.3
8 | 7.8 | 4 | 6.6
9 | 8.3 | 4.3 | 6.3
10 | 9.8 | 5.4 | 7.1
11 | 11.6 | 7 | 8
12 | 13.1 | 8.3 | 8.3
13 | 13.2 | 8.3 | 8.6
14 | 13.1 | 8.4 | 8.3
15 | 13.1 | 8.1 | 8.5
16 | 12.8 | 8.2 | 8.5
17 | 12.1 | 7.1 | 8.2
18 | 10.9 | 6.4 | 7.7
19 | 11 | 6 | 7.2
20 | 10.5 | 5.8 | 8
21 | 9.7 | 5.5 | 7.3
22 | 10.1 | 5.2 | 6.7
23 | 9.2 | 4 | 6.9
0 | 8.3 | 1.7 | 7
1 | 7.6 | 3.2 | 6.9
2 | 7 | 3.1 | 6.9
3 | 6.1 | 3 | 7
4 | 5.2 | 2.8 | 6.9
5 | 5.8 | 2.7 | 6.9
6 | 6.4 | 2.7 | 7
7 | 6.4 | 2.7 | 6.8
8 | 6.2 | 2.7 | 6.6
9 | 6.2 | 3 | 7.2
10 | 8.9 | 4 | 7.7
11 | 10.8 | 5.4 | 8.7
12 | 12 | 6.7 | 8.7
13 | 12 | 6.8 | 8.3
14 | 12 | 6.8 | 8.4
15 | 12.1 | 6.5 | 8.6
16 | 11.8 | 6.6 | 8.8
17 | 10.6 | 5.6 | 8.6
18 | 9.9 | 4.9 | 8.1
19 | 9.2 | 4.6 | 7.9
20 | 8.8 | 4.3 | 7.8
21 | 8.4 | 4.1 | 8.1
22 | 7.7 | 3.8 | 7.2
23 | 9.6 | 2.7 | 6.7
0 | 11.5 | 2.1 | 6.3
1 | 12.8 | 3.5 | 5.4
2 | 13.8 | 3.4 | 4.8
3 | 12.9 | 3.3 | 4.9
4 | 12.6 | 3.1 | 4
5 | 13 | 3 | 4
6 | 12.3 | 3 | 3.9
7 | 11.5 | 3 | 3.8
8 | 12.3 | 3 | 4
9 | 13 | 3.3 | 4.2
10 | 14.3 | 4.1 | 5.2
11 | 17.3 | 5.4 | 6.3
12 | 18.2 | 6.5 | 6.5
13 | 18.2 | 6.3 | 6.7
14 | 18.3 | 6.6 | 6.4
15 | 18.2 | 6.5 | 6.3
16 | 18.2 | 6.5 | 6.3
17 | 17 | 5.6 | 6.2
18 | 16.3 | 4.9 | 5.9
19 | 15.4 | 4.7 | 5.3
20 | 15.6 | 4.5 | 4.9
21 | 15.3 | 4.2 | 4.7
22 | 14.8 | 4 | 4.9
23 | 14.1 | 3 | 4.9
0 | 13.3 | 1.6 | 4.8
1 | 12.9 | 2.3 | 4.9
2 | 12.4 | 2.3 | 4.8
3 | 11.8 | 2.2 | 4.8
4 | 12 | 2.1 | 4.3
5 | 12.1 | 2.1 | 4
6 | 12.2 | 2.1 | 3.8
7 | 12.7 | 2.1 | 4.1
8 | 12.1 | 2.1 | 4.5
9 | 12.1 | 2.2 | 4.8
10 | 12.6 | 2.7 | 5.4
11 | 14 | 3.4 | 6.8
12 | 14.1 | 4 | 7.6
13 | 14.2 | 3.7 | 7.8
14 | 13.9 | 4.1 | 7.4
15 | 14.4 | 4.1 | 7.5
16 | 14 | 4 | 7.7
17 | 14 | 3.5 | 6.9
18 | 13.8 | 3.2 | 6.7
19 | 13.1 | 3 | 6.4
20 | 13.2 | 2.9 | 6.2
21 | 12.9 | 2.8 | 5.5
22 | 13.1 | 2.6 | 5.4
23 | 13 | 2.1 | 5.9
0 | 12.8 | 4.1 | 6.3
1 | 12.5 | 4.7 | 6.8
2 | 12.3 | 4.7 | 7.1
3 | 12.1 | 4.6 | 7.3
4 | 12.3 | 4.6 | 7.3
5 | 12 | 4.5 | 6.9
6 | 11.8 | 4.5 | 6.3
7 | 11.6 | 4.5 | 6.6
8 | 11.9 | 4.5 | 6.8
9 | 12.2 | 4.6 | 7.7
10 | 12.9 | 5 | 8.3
11 | 14 | 5.6 | 9.1
12 | 13.9 | 6.1 | 9.9
13 | 13.8 | 5.8 | 10
14 | 13.9 | 6.2 | 9.9
15 | 14.1 | 5.9 | 9.9
16 | 13.7 | 6.1 | 10
17 | 13.8 | 5.7 | 9.3
18 | 12.4 | 5.4 | 9.2
19 | 13.1 | 5.3 | 8.3
20 | 12.7 | 5.2 | 8.7
21 | 11.9 | 5.1 | 7.7
22 | 12.7 | 5 | 8
23 | 11.7 | 4.5 | 8.1
0 | 10.6 | 1 | 8.2
1 | 8.2 | 3.7 | 8.3
2 | 6.6 | 3.5 | 8.6
3 | 5.5 | 3.3 | 8.2
4 | 4.4 | 3 | 7.4
5 | 3.4 | 2.8 | 7.5
6 | 4.1 | 2.8 | 7
7 | 4.9 | 2.8 | 6.5
8 | 5 | 2.8 | 7.2
9 | 5.7 | 3.3 | 7.8
10 | 8.6 | 5 | 8.9
11 | 11.1 | 7.4 | 10.6
12 | 13.7 | 9.5 | 11.3
13 | 13.7 | 9.7 | 11.9
14 | 14.1 | 9.7 | 12
15 | 14 | 9.7 | 11.6
16 | 14 | 9.4 | 11.9
17 | 11.5 | 7.7 | 11.1
18 | 10.4 | 6.5 | 10.4
19 | 10 | 5.9 | 9.5
20 | 8.7 | 5.6 | 9.2
21 | 8.3 | 5.1 | 9.2
22 | 7.8 | 4.7 | 8.6
23 | 7.6 | 2.7 | 7.8
0 | 7.3 | 2.6 | 7
1 | 8 | 4.5 | 5.6
2 | 8.5 | 4.4 | 4.4
3 | 8.2 | 4.2 | 5.1
4 | 7.8 | 4 | 4.5
5 | 7.3 | 3.9 | 4.6
6 | 7.5 | 3.9 | 3.9
7 | 7.6 | 3.9 | 3.3
8 | 8.1 | 3.8 | 3.7
9 | 8.2 | 4.2 | 4.2
10 | 8.9 | 5.4 | 4.9
11 | 9.6 | 7 | 7.3
12 | 10.6 | 8.5 | 9
13 | 10.4 | 8.3 | 9.1
14 | 10.3 | 8.6 | 9.2
15 | 10.6 | 8.4 | 9.1
16 | 10.3 | 8.4 | 8.8
17 | 10.3 | 7.2 | 8.1
18 | 9.3 | 6.4 | 7.3
19 | 9.7 | 6 | 6.5
20 | 9 | 5.8 | 6.5
21 | 9 | 5.5 | 6.4
22 | 8.5 | 5.2 | 6.4
23 | 8.4 | 3.8 | 6.8
0 | 8.3 | 5.4 | 7.2
1 | 7.2 | 5.8 | 7.5
2 | 6.6 | 5.7 | 7.7
3 | 5.8 | 5.7 | 7.8
4 | 5.7 | 5.7 | 8.2
5 | 5.7 | 5.7 | 7.8
6 | 5.5 | 5.7 | 7.2
7 | 5.3 | 5.7 | 7.6
8 | 5.5 | 5.7 | 7.9
9 | 5.7 | 5.7 | 7.7
10 | 7.3 | 5.9 | 8.3
11 | 8.8 | 6.2 | 9.5
12 | 9.1 | 6.5 | 10
13 | 8.9 | 6.1 | 9.9
14 | 8.8 | 6.5 | 10.1
15 | 9.2 | 5.9 | 9.7
16 | 8.7 | 6.5 | 10
17 | 8.5 | 6.3 | 9.5
18 | 7.9 | 6.1 | 9.8
19 | 7.1 | 6 | 9.2
20 | 7 | 6 | 7.9
21 | 7.3 | 5.9 | 8.7
22 | 7.5 | 5.9 | 8.3
23 | 6.8 | 5.7 | 7.9
0 | 6 | 5 | 7.5
1 | 5.8 | 6.7 | 6.4
2 | 5.4 | 6.6 | 5.6
3 | 4.6 | 6.5 | 6
4 | 5.6 | 6.3 | 5.3
5 | 5.2 | 6.1 | 4.6
6 | 5.2 | 6.1 | 5.1
7 | 4.4 | 6.1 | 5.7
8 | 3.6 | 6.1 | 4.8
9 | 6 | 6.4 | 5.3
10 | 8.4 | 7.5 | 6.3
11 | 9.3 | 9.1 | 7.8
12 | 11.4 | 10.5 | 8.8
13 | 11.4 | 10.6 | 8.5
14 | 11.4 | 10.6 | 8.6
15 | 11.5 | 10.5 | 9
16 | 11 | 10.4 | 8.9
17 | 9.4 | 9.3 | 8.4
18 | 8.5 | 8.5 | 7.1
19 | 7.9 | 8.2 | 7.7
20 | 7.6 | 7.9 | 6.9
21 | 7.1 | 7.6 | 6.5
22 | 7.5 | 7.3 | 6.4
23 | 6.5 | 6.1 | 6
0 | 5.5 | 2 | 5.6
1 | 5.1 | 5.1 | 4.6
2 | 4.7 | 4.9 | 4
3 | 5 | 4.7 | 3.7
4 | 4.9 | 4.3 | 3.9
5 | 5 | 4.1 | 3.4
6 | 4.8 | 4.1 | 2.9
7 | 4.7 | 4.1 | 3.3
8 | 4.5 | 4 | 3.6
9 | 4.6 | 4.6 | 4.2
10 | 4.7 | 6.6 | 4.7
11 | 5.9 | 9.4 | 6
12 | 5.6 | 11.9 | 6.5
13 | 5.9 | 12.1 | 6.9
14 | 6 | 12.1 | 7.2
15 | 5.9 | 11.8 | 6.7
16 | 5.7 | 11.7 | 6.9
17 | 5.9 | 9.7 | 6.2
18 | 5.4 | 8.3 | 5.7
19 | 5.5 | 7.7 | 5.7
20 | 5.2 | 7.3 | 5.7
21 | 5.3 | 6.7 | 5.3
22 | 4.9 | 6.2 | 4.7
23 | 4.7 | 4 | 4.3
0 | 4.5 | 5 | 3.9
1 | 4.1 | 5.9 | 3.5
2 | 3.8 | 5.9 | 3.4
3 | 4.1 | 5.8 | 3.6
4 | 3.2 | 5.7 | 3.5
5 | 2.7 | 5.6 | 3.5
6 | 3 | 5.6 | 3.5
7 | 2.3 | 5.6 | 3.6
8 | 1.6 | 5.6 | 3.5
9 | 3.7 | 5.8 | 3.5
10 | 5.8 | 6.4 | 3.5
11 | 8.6 | 7.3 | 3.5
12 | 9.5 | 8 | 3.6
13 | 9.9 | 7.8 | 3.6
14 | 10.1 | 8.1 | 3.5
15 | 9.9 | 8.1 | 3.6
16 | 9.7 | 8 | 3.6
17 | 8.5 | 7.4 | 3.5
18 | 7.4 | 6.9 | 3.5
19 | 7 | 6.7 | 3.5
20 | 6.5 | 6.6 | 3.5
21 | 5.5 | 6.4 | 3.5
22 | 5 | 6.3 | 3.6
23 | 5.7 | 5.6 | 3.5
0 | 6.3 | 4 | 3.3
1 | 7.1 | 5.7 | 3.1
2 | 7.7 | 5.6 | 2.9
3 | 7.5 | 5.5 | 3
4 | 7.3 | 5.3 | 2.4
5 | 6.9 | 5.1 | 2.4
6 | 6.3 | 5.1 | 2.2
7 | 7.1 | 5.1 | 2
8 | 7.6 | 5.1 | 1.8
9 | 7.7 | 5.5 | 2.5
10 | 9.1 | 6.6 | 3.2
11 | 10.4 | 8.1 | 4.5
12 | 11.5 | 9.5 | 4.3
13 | 11.6 | 9.6 | 4.9
14 | 11.5 | 9.6 | 5.2
15 | 11.4 | 9.6 | 5.1
16 | 11.4 | 9.4 | 4.8
17 | 10.3 | 8.3 | 4.9
18 | 9.9 | 7.5 | 4.1
19 | 9.9 | 7.2 | 3.7
20 | 9.2 | 6.9 | 3.7
21 | 9.2 | 6.6 | 3.6
22 | 8.4 | 6.4 | 2.9
23 | 7.7 | 5.1 | 3
0 | 6.9 | 2 | 3
1 | 5.5 | 4 | 3.3
2 | 4.4 | 3.9 | 3.2
3 | 3.6 | 3.7 | 3.1
4 | 2.9 | 3.5 | 3.6
5 | 2.5 | 3.4 | 3.9
6 | 2.1 | 3.4 | 3
7 | 2.7 | 3.4 | 3.1
8 | 3.4 | 3.3 | 2.9
9 | 3.3 | 3.7 | 2.7
10 | 5.6 | 5.1 | 3.7
11 | 7.8 | 6.9 | 4.6
12 | 9.2 | 8.6 | 5.3
13 | 9.3 | 8.3 | 5.4
14 | 9.2 | 8.7 | 5.5
15 | 9.4 | 8.5 | 5.2
16 | 9.3 | 8.5 | 5.3
17 | 8.1 | 7.2 | 5.4
18 | 7.1 | 6.2 | 4.2
19 | 5.4 | 5.8 | 4.5
20 | 5.9 | 5.5 | 4.3
21 | 4.9 | 5.1 | 4
22 | 5.2 | 4.8 | 4.1
23 | 4.6 | 3.3 | 4
0 | 3.9 | 6 | 4
1 | 3.5 | 7.1 | 4.2
2 | 3 | 7.1 | 4.2
3 | 3 | 7 | 4.1
4 | 2.3 | 6.8 | 4
5 | 2.9 | 6.8 | 3.9
6 | 2.9 | 6.8 | 4.2
7 | 2.3 | 6.8 | 4.5
8 | 1.7 | 6.7 | 4.1
9 | 2.6 | 7 | 4.5
10 | 3.5 | 7.7 | 4.2
11 | 5.5 | 8.7 | 4.3
12 | 5.9 | 9.7 | 4.7
13 | 6.3 | 9.6 | 4.8
14 | 6.3 | 9.8 | 4.9
15 | 6.4 | 9.4 | 4.8
16 | 6.1 | 9.6 | 4.5
17 | 4.9 | 8.9 | 4.6
18 | 4.9 | 8.3 | 4.6
19 | 4.4 | 8.1 | 4.4
20 | 4.2 | 8 | 4.7
21 | 3.5 | 7.8 | 4.7
22 | 3.8 | 7.6 | 4
23 | 3.9 | 6.7 | 4.2
0 | 3.9 | 4.4 | 4.4
1 | 4.7 | 5.6 | 4.1
2 | 5.2 | 5.5 | 4.1
3 | 4.9 | 5.5 | 4.2
4 | 4.4 | 5.3 | 4
5 | 3.7 | 5.2 | 3.7
6 | 4.4 | 5.2 | 3.6
7 | 4.9 | 5.2 | 3.5
8 | 4.9 | 5.2 | 3.7
9 | 4.7 | 5.4 | 3.8
10 | 6.6 | 6.2 | 3.7
11 | 8.2 | 7.3 | 4.5
12 | 9.1 | 8.3 | 4.8
13 | 9.1 | 8.3 | 5
14 | 9 | 8.4 | 5
15 | 9.2 | 8.3 | 4.5
16 | 9.1 | 8.3 | 4.9
17 | 8.4 | 7.5 | 4.6
18 | 7.2 | 6.9 | 4.6
19 | 6.7 | 6.7 | 4.3
20 | 6.4 | 6.5 | 4.1
21 | 7.1 | 6.3 | 4.4
22 | 5.7 | 6.1 | 4
23 | 5.9 | 5.2 | 4.8
0 | 6 | 3.4 | 5.6
1 | 6.3 | 6.3 | 5.6
2 | 6.5 | 6.1 | 5.7
3 | 6 | 5.9 | 5.6
4 | 5.6 | 5.5 | 5.9
5 | 5.7 | 5.3 | 6
6 | 5.6 | 5.3 | 5.7
7 | 5.4 | 5.3 | 6
8 | 5.1 | 5.3 | 6
9 | 6.1 | 5.8 | 5.9
10 | 7 | 7.6 | 5.8
11 | 8.6 | 10.2 | 5.7
12 | 9.1 | 12.5 | 6
13 | 9.1 | 12.6 | 5.7
14 | 9.1 | 12.6 | 5.6
15 | 9.2 | 12.7 | 5.6
16 | 9 | 12.3 | 5.9
17 | 8.4 | 10.5 | 5.7
18 | 7.9 | 9.2 | 5.7
19 | 7.7 | 8.6 | 5.6
20 | 6.8 | 8.3 | 5.6
21 | 7.4 | 7.8 | 5.7
22 | 7.1 | 7.3 | 5.7
23 | 5.8 | 7.4 | 5.4
0 | 4.4 | 7.4 | 5.1
1 | 3.1 | 7.5 | 4.8
2 | 1.7 | 7.6 | 4.5
3 | 1 | 7.5 | 4
4 | 1.7 | 7.4 | 2.7
5 | 2.3 | 7.3 | 1.5
6 | 2.2 | 7.3 | 2.2
7 | 1.5 | 6.6 | 3
8 | 1.4 | 7.3 | 2.8
9 | 2.4 | 7.7 | 3.7
10 | 4.4 | 8.5 | 6
11 | 5.4 | 9.4 | 9
12 | 6 | 10.2 | 11.1
13 | 6.1 | 9.9 | 11.2
14 | 6.6 | 10.1 | 11.2
15 | 6.4 | 9.7 | 11.6
16 | 6.5 | 10.2 | 11.5
17 | 6.2 | 9.5 | 10.6
18 | 4.9 | 8.9 | 8.4
19 | 4.3 | 8.5 | 7.7
20 | 3.6 | 8.3 | 6.8
21 | 3.7 | 8 | 6.1
22 | 3.7 | 7.8 | 4.9
23 | 2.8 | 7.1 | 5.3
0 | 1.8 | 6.5 | 5.8
1 | 1 | 7.4 | 6.4
2 | 0.6 | 7.2 | 6.9
3 | -0.9 | 7 | 6.3
4 | -1.1 | 6.8 | 7.2
5 | 0 | 6.8 | 6.9
6 | -1.2 | 6.7 | 6.5
7 | -2.4 | 5.6 | 6.2
8 | -1.3 | 6.6 | 5.8
9 | -0.3 | 7.3 | 7.1
10 | 3.8 | 8.6 | 8.4
11 | 5.7 | 10.2 | 8.8
12 | 7.7 | 11.4 | 9.9
13 | 7.7 | 11.4 | 9.7
14 | 7.9 | 11.4 | 10
15 | 7.5 | 11.2 | 10
16 | 7.8 | 11.4 | 9.9
17 | 6.2 | 10.3 | 9.6
18 | 4.8 | 9.3 | 9.5
19 | 3.7 | 8.7 | 7.7
20 | 3.4 | 8.3 | 7.8
21 | 2.2 | 7.9 | 7.2
22 | 1.9 | 7.6 | 8.1
23 | 1.8 | 6.5 | 7.2
0 | 1.8 | 5.9 | 6.4
1 | 1.8 | 6.9 | 5.5
2 | 1.8 | 6.7 | 5.1
3 | 2.3 | 6.5 | 4.6
4 | 2.7 | 6.3 | 4.4
5 | 3.6 | 6.2 | 3.8
6 | 4 | 6.2 | 3.2
7 | 3.4 | 4.8 | 4.2
8 | 2.9 | 6.1 | 5.2
9 | 3.9 | 6.8 | 6
10 | 6.4 | 8.3 | 6.2
11 | 8 | 10.1 | 9.9
12 | 8.5 | 11.4 | 11.1
13 | 8.8 | 11.1 | 11
14 | 8.8 | 11.4 | 11.3
15 | 8.9 | 11.3 | 11.1
16 | 8.8 | 11.5 | 11.2
17 | 8.7 | 10.2 | 10.3
18 | 6.2 | 9 | 8.7
19 | 6.2 | 8.4 | 7.6
20 | 5.9 | 8 | 7.1
21 | 4.8 | 7.5 | 7
22 | 4.6 | 7.2 | 5.8
23 | 4.1 | 5.9 | 5.8
0 | 3.7 | 4.3 | 5.8
1 | 3.3 | 5 | 5.4
2 | 2.5 | 4.9 | 5.3
3 | 3.6 | 4.7 | 3.8
4 | 3.2 | 4.6 | 4.1
5 | 2.5 | 4.6 | 3
6 | 1.6 | 4.5 | 2.9
7 | 2.3 | 3.6 | 2.6
8 | 2.9 | 4.5 | 2.3
9 | 3.3 | 5 | 4
10 | 4.1 | 6 | 5.8
11 | 7 | 7.2 | 8.1
12 | 7.7 | 8.1 | 10
13 | 7.9 | 8 | 10.4
14 | 7.5 | 8.1 | 10.1
15 | 7.7 | 8 | 10.4
16 | 7.5 | 8.2 | 10.4
17 | 7.5 | 7.3 | 9.1
18 | 5.9 | 6.5 | 8.2
19 | 5.1 | 6.1 | 7
20 | 4.6 | 5.8 | 6.9
21 | 3.6 | 5.5 | 6.1
22 | 4.5 | 5.2 | 6.1
23 | 3.6 | 4.4 | 5.2
0 | 2.7 | 3 | 4.2
1 | 1.5 | 3.8 | 4.4
2 | 0.6 | 3.6 | 3.8
3 | 0.8 | 3.4 | 3.6
4 | -0.2 | 3.3 | 3.3
5 | -0.4 | 3.3 | 3.9
6 | -0.7 | 3.2 | 4.4
7 | -0.1 | 2.2 | 4.2
8 | 0.5 | 3.1 | 3.7
9 | 0.6 | 3.7 | 4
10 | 2.3 | 4.9 | 7.4
11 | 3 | 6.2 | 6.6
12 | 5.2 | 7.2 | 7.8
13 | 5.2 | 7.1 | 8
14 | 5.3 | 7.2 | 8
15 | 5 | 7 | 8.1
16 | 5.1 | 7.3 | 8
17 | 4.6 | 6.3 | 6.9
18 | 3.3 | 5.4 | 7.2
19 | 3.3 | 4.9 | 5.8
20 | 2.3 | 4.6 | 5.5
21 | 1.9 | 4.2 | 4.9
22 | 1.2 | 4 | 6.3
23 | 1.6 | 3 | 4.9
0 | 2 | 4.2 | 3.5
1 | 2.3 | 5.2 | 2
2 | 2.8 | 5 | 1
3 | 1.6 | 4.8 | 1.3
4 | 0.3 | 4.7 | 1.5
5 | 0.6 | 4.6 | 0.9
6 | 0.9 | 4.5 | 0.4
7 | 1.4 | 3.3 | 0.5
8 | 1.7 | 4.5 | 0.7
9 | 2.3 | 5.1 | 1.2
10 | 4.7 | 6.5 | 1.6
11 | 5.7 | 8.1 | 3.4
12 | 7.3 | 9.3 | 4.5
13 | 7.2 | 8.9 | 4.5
14 | 7.4 | 9.3 | 4.2
15 | 7.2 | 9 | 4.1
16 | 7.1 | 9.3 | 4.2
17 | 6.6 | 8.2 | 4
18 | 5.6 | 7.1 | 3.9
19 | 3.9 | 6.5 | 2.6
20 | 4.4 | 6.2 | 3.3
21 | 3.1 | 5.8 | 1.8
22 | 3.1 | 5.4 | 2
23 | 2.6 | 4.3 | 2.3
0 | 2.2 | -1.5 | 2.5
1 | 2.3 | -0.8 | 2.5
2 | 2.4 | -0.9 | 2.3
3 | 1.1 | -1.1 | 1.6
4 | 1.8 | -1.2 | 2.3
5 | 1.8 | -1.2 | 1.8
6 | 1.1 | -1.3 | 0.9
7 | 0.3 | -2.2 | 0
8 | 1 | -1.3 | 1.2
9 | 1.7 | -0.8 | 2.5
10 | 4.4 | 0.2 | 3.9
11 | 5.7 | 1.4 | 6.5
12 | 7.2 | 2.3 | 8.1
13 | 7.2 | 2.2 | 8.1
14 | 7.4 | 2.3 | 8.4
15 | 7.3 | 2.1 | 8.3
16 | 7 | 2.3 | 8.1
17 | 6.7 | 1.5 | 7.5
18 | 6.2 | 0.7 | 5.9
19 | 4.1 | 0.2 | 4.1
20 | 3.7 | -0.1 | 4.6
21 | 2.8 | -0.4 | 3.3
22 | 3.4 | -0.6 | 2.8
23 | 2.4 | -1.5 | 2.3
0 | 1.3 | 2.2 | 1.8
1 | 0 | 2.9 | 1.7
2 | -1.3 | 2.8 | 1.7
3 | -1.8 | 2.6 | 0.5
4 | -1.3 | 2.5 | 1.3
5 | -2.1 | 2.4 | 0.7
6 | -2.8 | 2.4 | -0.4
7 | -2.2 | 1.4 | -1.6
8 | -1.5 | 2.3 | -0.3
9 | -1.3 | 2.9 | 0.9
10 | 0.1 | 4 | 3.4
11 | 1.2 | 5.3 | 5.8
12 | 3.6 | 6.3 | 8.3
13 | 3.8 | 6 | 8.6
14 | 3.6 | 6.3 | 8.7
15 | 3.6 | 6.2 | 8.4
16 | 3.4 | 6.3 | 8.5
17 | 2.4 | 5.4 | 7.5
18 | 2.4 | 4.5 | 5.7
19 | 1.3 | 4 | 4.4
20 | 0.6 | 3.7 | 3.5
21 | -0.2 | 3.4 | 2.8
22 | -0.3 | 3.1 | 3.1
23 | 1 | 2.2 | 2
0 | 2.2 | 0.1 | 0.8
1 | 2.9 | 0.5 | 0.3
2 | 3.4 | 0.4 | 0.1
3 | 3.5 | 0.3 | 0.2
4 | 3.1 | 0.3 | -0.5
5 | 2.8 | 0.2 | 0.9
6 | 2.6 | 0.2 | -0.8
7 | 2.2 | -0.2 | -2.4
8 | 2.9 | 0.2 | -1.1
9 | 3.4 | 0.4 | 0.2
10 | 4.1 | 0.9 | 1.5
11 | 5.8 | 1.5 | 4.9
12 | 6.5 | 2 | 6.5
13 | 6.3 | 1.5 | 7.2
14 | 6.7 | 2 | 7.1
15 | 6.5 | 1.9 | 7.1
16 | 6.6 | 2 | 7.1
17 | 6.4 | 1.6 | 6.5
18 | 5.7 | 1.2 | 4.1
19 | 5.9 | 1 | 2.7
20 | 3.7 | 0.8 | 1.8
21 | 4.2 | 0.7 | 1.8
22 | 4.1 | 0.5 | 1.3
23 | 4.2 | 0.1 | 0.7
0 | 4.3 | 2.4 | 0
1 | 4.2 | 2.7 | -0.2
2 | 4.2 | 2.6 | -0.7
3 | 3.2 | 2.6 | -0.9
4 | 3.2 | 2.5 | -0.7
5 | 3 | 2.5 | -0.6
6 | 2.8 | 2.5 | -1.2
7 | 3.2 | 2.2 | -2.3
8 | 3.7 | 2.5 | -3.5
9 | 3.6 | 2.7 | 0
10 | 4.6 | 3 | 3.6
11 | 4.8 | 3.4 | 6.3
12 | 6 | 3.7 | 8.7
13 | 6 | 3.3 | 9.3
14 | 6.3 | 3.7 | 9.3
15 | 5.9 | 3.3 | 9.4
16 | 6.2 | 3.7 | 9.3
17 | 5.5 | 3.4 | 7.6
18 | 5.3 | 3.2 | 6.1
19 | 5.3 | 3 | 3.8
20 | 3.9 | 2.9 | 2.9
21 | 4.5 | 2.8 | 2.7
22 | 4.6 | 2.7 | 1.7
23 | 4 | 2.4 | 0.4
0 | 3.3 | -0.1 | -0.9
1 | 2.6 | 0.4 | -1
2 | 2 | 0.3 | -0.9
3 | 2.4 | 0.2 | -1.6
4 | 2.1 | 0.1 | -2.5
5 | 1.8 | 0.1 | -2.2
6 | 1.4 | 0 | -3.3
7 | 2.3 | -0.5 | -4.3
8 | 3.2 | 0 | -2.8
9 | 1.8 | 0.3 | -1.3
10 | 3.5 | 1 | 0.1
11 | 4.1 | 1.8 | 4.8
12 | 5.3 | 2.4 | 6.2
13 | 4.9 | 2.3 | 6.3
14 | 5.1 | 2.4 | 6.4
15 | 5.1 | 2.2 | 6.5
16 | 5 | 2.4 | 6.4
17 | 5.2 | 1.8 | 5.7
18 | 4.1 | 1.3 | 3
19 | 3.8 | 1 | 1.8
20 | 3.3 | 0.8 | 1
21 | 3 | 0.6 | 0.7
22 | 2.3 | 0.5 | -0.9
23 | 2.8 | -0.1 | -1.3
0 | 3.3 | -0.8 | -1.6
1 | 3.9 | 0.6 | -1.6
2 | 3.8 | 0.4 | -1.6
3 | 4.1 | 0 | -1.6
4 | 3.2 | -0.2 | -1.9
5 | 3.2 | -0.3 | -2.5
6 | 3.3 | -0.4 | -3.1
7 | 2.3 | -2.3 | -2.3
8 | 1.2 | -0.5 | -1.6
9 | 4.2 | 0.5 | -0.7
10 | 7.1 | 2.6 | -0.1
11 | 9.9 | 5.1 | 2.4
12 | 12 | 7 | 3.5
13 | 12.3 | 6.9 | 3.6
14 | 12.4 | 7 | 3.6
15 | 12.3 | 7.1 | 3.7
16 | 12.3 | 7 | 3.6
17 | 12.3 | 5.3 | 2.3
18 | 8.6 | 3.7 | 2
19 | 7.8 | 2.7 | 1
20 | 7.3 | 2.1 | 0.4
21 | 5.8 | 1.5 | -0.1
22 | 5 | 1 | -0.4
23 | 4.9 | -0.8 | -1.1
0 | 4.9 | 3.9 | -1.8
1 | 5.4 | 4.4 | -2.2
2 | 5.6 | 4.3 | -3
3 | 6 | 4.2 | -1.5
4 | 5.8 | 4.1 | -2.1
5 | 5.3 | 4.1 | -3.4
6 | 4.9 | 4.1 | -3.7
7 | 4.4 | 3.5 | -4.1
8 | 5.5 | 4 | -2.3
9 | 6.6 | 4.4 | -0.7
10 | 7 | 5 | 0.6
11 | 9.6 | 5.8 | 3.2
12 | 10.3 | 6.4 | 4.6
13 | 10.2 | 5.9 | 4.4
14 | 10.6 | 6.4 | 4.6
15 | 10.5 | 6 | 4.7
16 | 10.4 | 6.4 | 4.4
17 | 10.2 | 5.9 | 4.5
18 | 8.6 | 5.4 | 1.9
19 | 8.5 | 5.1 | 1.6
20 | 8 | 4.9 | -0.2
21 | 7.5 | 4.7 | -0.4
22 | 6.6 | 4.5 | -0.8
23 | 6.4 | 3.9 | -0.8
0 | 6.3 | 3.8 | -0.8
1 | 5.5 | 4.7 | 0
2 | 4.6 | 4.5 | 0.5
3 | 5.3 | 4.3 | 0.5
4 | 4.4 | 4.2 | -0.7
5 | 3.6 | 4.1 | -0.4
6 | 4.1 | 4.1 | -1.3
7 | 4.5 | 2.9 | -2.4
8 | 4.4 | 4 | -1
9 | 5.7 | 4.6 | 0.2
10 | 7 | 6 | 3
11 | 7.8 | 7.5 | 6.2
12 | 8.9 | 8.7 | 7
13 | 8.9 | 8.7 | 7.8
14 | 9.3 | 8.7 | 7.6
15 | 9.2 | 8.4 | 7.9
16 | 9.3 | 8.7 | 7.6
17 | 8.9 | 7.6 | 7.6
18 | 7.6 | 6.6 | 5.1
19 | 6.5 | 6 | 4.4
20 | 6.4 | 5.6 | 3.2
21 | 5.8 | 5.3 | 2.2
22 | 5.2 | 4.9 | 1.1
23 | 5.4 | 3.8 | 0.9
0 | 5.6 | 3.2 | 0.8
1 | 5.7 | 4 | 1.4
2 | 6.1 | 3.8 | 1.6
3 | 4.7 | 3.7 | 1.4
4 | 3.3 | 3.5 | 2
5 | 3.7 | 3.5 | 1.2
6 | 4.1 | 3.4 | 0.2
7 | 3.7 | 2.4 | 0.7
8 | 3.9 | 3.4 | 1
9 | 4.4 | 3.9 | 1.9
10 | 5.9 | 5.1 | 3.8
11 | 8.1 | 6.5 | 5.2
12 | 9.6 | 7.5 | 6.7
13 | 9.4 | 7.1 | 6.2
14 | 9.6 | 7.5 | 6.7
15 | 9.7 | 7.1 | 6.8
16 | 9.4 | 7.5 | 6.7
17 | 9.6 | 6.5 | 6
18 | 7.5 | 5.7 | 5
19 | 7 | 5.1 | 4.2
20 | 6.5 | 4.8 | 4.2
21 | 6 | 4.5 | 3.1
22 | 5.4 | 4.2 | 3
23 | 6.9 | 3.2 | 3.2
0 | 8.3 | 5.4 | 3.3
1 | 8.5 | 5.8 | 3.6
2 | 8.6 | 5.7 | 3.6
3 | 8.7 | 5.6 | 3.6
4 | 8.6 | 5.5 | 4
5 | 8.5 | 5.5 | 3.8
6 | 8.3 | 5.5 | 3
7 | 8.6 | 4.9 | 2.2
8 | 8.8 | 5.5 | 4
9 | 8.4 | 6 | 5.7
10 | 8.8 | 6.8 | 7.3
11 | 9.9 | 7.6 | 9
12 | 9.8 | 8.2 | 11
13 | 9.7 | 8 | 11.3
14 | 9.9 | 8.3 | 11.2
15 | 9.5 | 8.2 | 11.2
16 | 10 | 8.1 | 11
17 | 9.3 | 7.8 | 10.2
18 | 9.6 | 7.2 | 9.3
19 | 9.6 | 6.8 | 7.5
20 | 9.1 | 6.5 | 7
21 | 9.1 | 6.4 | 6.6
22 | 9.6 | 6.2 | 6.1
23 | 9.4 | 5.6 | 5.7
0 | 9.2 | 2.7 | 5.3
1 | 8.8 | 3.4 | 5.3
2 | 8.3 | 3.3 | 5
3 | 7.9 | 3.1 | 5.4
4 | 7.6 | 3 | 5.2
5 | 7.2 | 2.9 | 4.9
6 | 6.7 | 2.8 | 5
7 | 7.4 | 1.6 | 5.1
8 | 8.1 | 2.9 | 5.3
9 | 9.3 | 4 | 6.1
10 | 11.7 | 5.7 | 6.4
11 | 13.3 | 7.5 | 7.8
12 | 13.4 | 8.6 | 8
13 | 14.1 | 8.5 | 8.1
14 | 14.1 | 8.7 | 8.2
15 | 13.7 | 8.5 | 8
16 | 14.1 | 8.5 | 8
17 | 13.8 | 7.8 | 8.1
18 | 12 | 6.6 | 7.8
19 | 10.5 | 5.6 | 6.8
20 | 10.3 | 5.1 | 7.1
21 | 10.3 | 4.8 | 6.4
22 | 9.6 | 4.5 | 6.7
23 | 8.7 | 3.1 | 6.3
0 | 7.9 | 3.3 | 5.9
1 | 7.3 | 3.6 | 5.6
2 | 6.8 | 3.6 | 4.6
3 | 6.7 | 3.5 | 3.6
4 | 6.7 | 3.4 | 4.1
5 | 6.9 | 3.4 | 4.6
6 | 7.1 | 3.4 | 4.8
7 | 7.1 | 2.9 | 4.5
8 | 7.1 | 3.4 | 4.6
9 | 7.8 | 3.8 | 5
10 | 9.5 | 4.5 | 7.7
11 | 9.7 | 5.2 | 8.2
12 | 10.5 | 5.7 | 8.9
13 | 10.3 | 5.4 | 9.8
14 | 10.6 | 5.8 | 9.9
15 | 10.7 | 5.6 | 9.8
16 | 10.6 | 5.6 | 9.8
17 | 10.4 | 5.4 | 9
18 | 10.5 | 4.9 | 8.1
19 | 8.5 | 4.5 | 7.2
20 | 8.4 | 4.3 | 6.4
21 | 8.7 | 4.2 | 6.3
22 | 8.9 | 4 | 6.3
23 | 8.1 | 3.5 | 6.5
0 | 7.3 | 2.1 | 6.6
1 | 5.9 | 2.3 | 7.6
2 | 4.7 | 2.3 | 8.4
3 | 3.7 | 2.2 | 7.6
4 | 3.8 | 2.2 | 7.6
5 | 4.6 | 2.1 | 7.2
6 | 4 | 2.1 | 6.6
7 | 3.4 | 1.7 | 7.3
8 | 4.4 | 2.1 | 7.8
9 | 5.5 | 2.5 | 9
10 | 6.6 | 3.1 | 9.4
11 | 8.9 | 3.6 | 11.3
12 | 9.3 | 4 | 11.4
13 | 9.3 | 3.5 | 12.2
14 | 9 | 4 | 12.3
15 | 9.4 | 3.6 | 12
16 | 9.3 | 3.7 | 12.2
17 | 9.2 | 3.7 | 12
18 | 7.5 | 3.3 | 10.7
19 | 6.5 | 3 | 10.3
20 | 5.4 | 2.9 | 9.2
21 | 6.2 | 2.8 | 9
22 | 5.7 | 2.7 | 9.4
23 | 5.3 | 2.2 | 8.7
0 | 4.9 | 2.7 | 8
1 | 5.1 | 3.1 | 6.7
2 | 5 | 3 | 5.7
3 | 4.4 | 2.9 | 5.6
4 | 3.7 | 2.9 | 5.4
5 | 4.4 | 2.8 | 5
6 | 5.1 | 2.8 | 4.7
7 | 4 | 2.2 | 4.8
8 | 4.4 | 2.8 | 5
9 | 5.3 | 3.4 | 5.9
10 | 7.2 | 4.3 | 6.8
11 | 8.5 | 5.2 | 7.9
12 | 9.7 | 5.8 | 8.3
13 | 9.6 | 5.7 | 9.3
14 | 9.8 | 5.9 | 9
15 | 9.9 | 5.6 | 9.4
16 | 9.7 | 5.5 | 9
17 | 9.8 | 5.4 | 9.1
18 | 8.7 | 4.8 | 8.5
19 | 7.6 | 4.3 | 8
20 | 7 | 4 | 7.1
21 | 6.4 | 3.8 | 7.3
22 | 6.3 | 3.7 | 6.8
23 | 6.1 | 2.9 | 6.5
0 | 5.8 | 4.8 | 6.3
1 | 6.2 | 5.6 | 5.6
2 | 6.4 | 5.4 | 4.9
3 | 6.1 | 5.2 | 4.4
4 | 5.8 | 5.1 | 5
5 | 6.1 | 5 | 4.2
6 | 6.3 | 4.9 | 3.5
7 | 7.1 | 3.6 | 3.8
8 | 6.3 | 5 | 4.1
9 | 6.9 | 6.2 | 5.4
10 | 8.2 | 8.2 | 5.9
11 | 8.4 | 10.2 | 7.8
12 | 9.5 | 11.5 | 8.5
13 | 9.5 | 11.6 | 9.2
14 | 9.6 | 11.6 | 9.3
15 | 9.3 | 11.4 | 8.9
16 | 9.2 | 11.5 | 9.2
17 | 9.3 | 10.6 | 9
18 | 8.9 | 9.2 | 7.5
19 | 8.7 | 8.1 | 7.4
20 | 8.4 | 7.5 | 5.7
21 | 7.6 | 7.1 | 5.7
22 | 7.2 | 6.8 | 5.8
23 | 6.8 | 5.2 | 4.7
0 | 6.3 | 5.1 | 3.6
1 | 5.4 | 5.8 | 2
2 | 4.3 | 5.6 | 0.6
3 | 4.4 | 5.5 | 1.5
4 | 4.5 | 5.3 | 0.7
5 | 4.1 | 5.3 | -0.1
6 | 3.6 | 5.2 | 0.2
7 | 3.1 | 4 | 0.4
8 | 5 | 5.3 | 0.7
9 | 6.8 | 6.3 | 1.5
10 | 9.3 | 8 | 2.7
11 | 10.6 | 9.7 | 4.4
12 | 11.7 | 10.9 | 4.7
13 | 12.7 | 10.9 | 5.7
14 | 12.7 | 11 | 5.2
15 | 12.8 | 10.8 | 5.8
16 | 12.4 | 10.6 | 5.7
17 | 12.4 | 10.1 | 5.4
18 | 10.3 | 8.9 | 3.3
19 | 8.9 | 8 | 4
20 | 8.5 | 7.4 | 3.2
21 | 7.6 | 7.1 | 2.6
22 | 6.6 | 6.8 | 2
23 | 6.7 | 5.5 | 2.9
0 | 6.9 | 4.5 | 3.8
1 | 7.1 | 5.1 | 4.6
2 | 7.2 | 5 | 4.3
3 | 8.8 | 4.8 | 3.8
4 | 6.8 | 4.7 | 4.4
5 | 7 | 4.7 | 4.8
6 | 6.7 | 4.6 | 4.6
7 | 6.7 | 3.5 | 4.4
8 | 6.5 | 4.7 | 4.3
9 | 7.4 | 5.6 | 5.9
10 | 8.2 | 7.2 | 6.4
11 | 9.8 | 8.7 | 7.6
12 | 9.8 | 9.7 | 8.5
13 | 10 | 9.7 | 8.6
14 | 10 | 9.8 | 8.3
15 | 9.8 | 9.7 | 8.6
16 | 10.1 | 9.5 | 8.7
17 | 10 | 9 | 8.4
18 | 8.6 | 7.9 | 7.7
19 | 8.1 | 7.1 | 6.7
20 | 8.1 | 6.6 | 6.3
21 | 8.6 | 6.3 | 6.1
22 | 8 | 6.1 | 6.2
23 | 7.8 | 4.8 | 5.4
0 | 7.7 | 2.6 | 4.6
1 | 7.1 | 3.5 | 3.2
2 | 6 | 3.3 | 1.7
3 | 4.9 | 3.1 | 2.8
4 | 5.5 | 2.9 | 1.7
5 | 6.1 | 2.9 | 1.6
6 | 6.1 | 2.8 | 1.5
7 | 5.8 | 1.4 | 2
8 | 5.6 | 2.9 | 2.5
9 | 6.8 | 4.1 | 3
10 | 8.1 | 6.2 | 3.8
11 | 9 | 8.3 | 5.2
12 | 10.6 | 9.7 | 5.2
13 | 10.6 | 9.6 | 5.6
14 | 11 | 9.8 | 5.7
15 | 10.7 | 9.7 | 5.3
16 | 10.7 | 9.6 | 5.6
17 | 10.6 | 8.7 | 5.6
18 | 8.9 | 7.2 | 5.2
19 | 8.7 | 6.1 | 3.8
20 | 8 | 5.5 | 2.7
21 | 7.5 | 5.1 | 2.7
22 | 7.4 | 4.7 | 3.2
23 | 8 | 3.1 | 3.7
0 | 8.5 | 4 | 4.2
1 | 8.8 | 4.6 | 4.8
2 | 8.7 | 4.4 | 4.6
3 | 8.5 | 4.3 | 4.2
4 | 8.6 | 4.2 | 4.6
5 | 8.6 | 4.1 | 4.8
6 | 8.7 | 4 | 5.8
7 | 9 | 3.1 | 5.2
8 | 8.6 | 4.1 | 5
9 | 8.8 | 5 | 5.7
10 | 9.6 | 6.4 | 7.1
11 | 10.2 | 7.8 | 7.7
12 | 10.1 | 8.8 | 8.6
13 | 10.3 | 8.7 | 8.9
14 | 10.4 | 8.9 | 9
15 | 10.3 | 8.6 | 8.9
16 | 10.5 | 8.8 | 8.9
17 | 10.3 | 8.1 | 8.4
18 | 9.4 | 7.1 | 8.3
19 | 9.8 | 6.3 | 7.2
20 | 9.9 | 5.9 | 6.5
21 | 10.3 | 5.7 | 6.4
22 | 9.2 | 5.4 | 6.2
23 | 9.5 | 4.3 | 6.3
0 | 9.8 | 3 | 6.4
1 | 9.7 | 3.4 | 6.4
2 | 9.9 | 3.3 | 6.4
3 | 10.2 | 3.2 | 6.4
4 | 10.8 | 3.1 | 6.2
5 | 9.5 | 3.1 | 5.5
6 | 10.2 | 3 | 4.8
7 | 9.8 | 2.4 | 5.3
8 | 10.4 | 3.1 | 5.7
9 | 10.1 | 3.7 | 5.8
10 | 12.6 | 4.8 | 7.8
11 | 13.5 | 5.8 | 9.2
12 | 14.3 | 6.5 | 10.3
13 | 14.5 | 6.2 | 10
14 | 14.4 | 6.6 | 10.4
15 | 14.2 | 6.6 | 10.2
16 | 14.6 | 6.6 | 10.3
17 | 13.8 | 6 | 9.8
18 | 13.8 | 5.3 | 8.2
19 | 12.7 | 4.7 | 8.5
20 | 12.1 | 4.4 | 8.1
21 | 11.3 | 4.2 | 7.3
22 | 10.7 | 4 | 7
23 | 10.2 | 3.2 | 6.2
0 | 9.8 | 2.1 | 5.4
1 | 8.6 | 2.9 | 4.6
2 | 7.6 | 2.7 | 3.8
3 | 7.7 | 2.5 | 3.6
4 | 7.5 | 2.4 | 2.8
5 | 7.2 | 2.3 | 2
6 | 6.9 | 2.2 | 2.6
7 | 7.2 | 1 | 3.2
8 | 7.5 | 2.3 | 3
9 | 7.9 | 3.4 | 4.7
10 | 9.7 | 5.3 | 6.4
11 | 10 | 7 | 8.1
12 | 11.1 | 8.3 | 9.5
13 | 11 | 8.3 | 10
14 | 10.6 | 8.4 | 10.1
15 | 11.1 | 8 | 10.2
16 | 10.9 | 8.3 | 9.8
17 | 11 | 7.5 | 8.9
18 | 10.6 | 6.1 | 7.7
19 | 9.7 | 5.2 | 6.8
20 | 8.8 | 4.6 | 6.5
21 | 8 | 4.3 | 6.2
22 | 8 | 4 | 5.6
23 | 8.7 | 2.5 | 5.7
0 | 9.4 | 0.8 | 5.8
1 | 9.5 | 1.8 | 6.6
2 | 9.3 | 1.6 | 7.1
3 | 9.5 | 1.4 | 6.2
4 | 9.5 | 1.2 | 5.2
5 | 9.2 | 1.1 | 6
6 | 9.5 | 1 | 6.8
7 | 9.2 | -0.6 | 6.1
8 | 8.9 | 1.1 | 6.2
9 | 10 | 2.6 | 8.7
10 | 11 | 4.9 | 9.2
11 | 10.9 | 7.2 | 11.2
12 | 12 | 8.8 | 12.5
13 | 12 | 8.9 | 12.5
14 | 11.9 | 8.9 | 12.7
15 | 12.1 | 8.7 | 12.6
16 | 11.9 | 8.7 | 12.6
17 | 11.8 | 7.7 | 12.2
18 | 11.5 | 6.1 | 11
19 | 10.5 | 4.8 | 9.4
20 | 10.1 | 4.1 | 9.6
21 | 10.2 | 3.7 | 8.3
22 | 11.2 | 3.2 | 8.2
23 | 10.4 | 4.2 | 6.9
0 | 10.6 | 5.2 | 5.7
1 | 10.3 | 6.1 | 4.4
2 | 9.7 | 7.1 | 3.2
3 | 10.3 | 6.8 | 3.1
4 | 10.6 | 6.7 | 2.9
5 | 10.8 | 6.5 | 3.3
6 | 10.5 | 6.3 | 2.9
7 | 11 | 5.3 | 2.5
8 | 11.5 | 7 | 3.6
9 | 13.2 | 8.7 | 4.8
10 | 14.9 | 10.7 | 5.5
11 | 16.9 | 12.4 | 6.8
12 | 17.7 | 13.5 | 7.2
13 | 17.5 | 13.4 | 7.2
14 | 17.8 | 13.8 | 7
15 | 17.7 | 13.7 | 7.3
16 | 17.7 | 13.5 | 7.1
17 | 17.6 | 12.9 | 7
18 | 15.5 | 11.5 | 5.9
19 | 14.8 | 10.3 | 5.5
20 | 13.9 | 9.4 | 4.8
21 | 12.7 | 9 | 4.6
22 | 12.5 | 8.5 | 4
23 | 12.3 | 7.2 | 4
0 | 12.1 | 11.3 | 4.1
1 | 11.2 | 11.6 | 4.9
2 | 10.5 | 11.4 | 5.4
3 | 10.3 | 11.3 | 4.6
4 | 10.5 | 11.3 | 4.7
5 | 10.1 | 11.2 | 5.1
6 | 9.8 | 11.1 | 4.6
7 | 10.3 | 10.7 | 4
8 | 10.9 | 11.4 | 5.5
9 | 11.6 | 12.1 | 6.8
10 | 12.9 | 13 | 7.8
11 | 14 | 13.7 | 10.3
12 | 14.1 | 14.2 | 10.6
13 | 14.5 | 13.8 | 10.7
14 | 14.4 | 14.3 | 10.8
15 | 14.1 | 13.9 | 10.7
16 | 14.1 | 14.1 | 10.7
17 | 14 | 13.9 | 10.2
18 | 12.7 | 13.3 | 9.8
19 | 12.4 | 12.8 | 7.9
20 | 12.7 | 12.4 | 7.6
21 | 12 | 12.2 | 6.9
22 | 11.8 | 12 | 6.5
23 | 10.9 | 11.5 | 6.5
0 | 10 | 5.9 | 6.5
1 | 8.7 | 6.4 | 6.4
2 | 8 | 6.1 | 6.1
3 | 7.9 | 5.9 | 6.4
4 | 7.9 | 5.8 | 6.3
5 | 7.9 | 5.6 | 5.8
6 | 7.7 | 5.4 | 5.2
7 | 7.5 | 4.6 | 5.6
8 | 8.1 | 6 | 5.9
9 | 8.7 | 7.5 | 8
10 | 8.5 | 9.2 | 8.8
11 | 8.9 | 10.7 | 10.3
12 | 9.4 | 11.7 | 11.2
13 | 9.4 | 11.6 | 11.2
14 | 9.8 | 11.9 | 11.3
15 | 9.6 | 11.8 | 11.2
16 | 9.5 | 11.6 | 10.8
17 | 9.2 | 11.1 | 10.2
18 | 8.9 | 9.9 | 10
19 | 9.3 | 8.8 | 8.7
20 | 7.9 | 8.1 | 7.9
21 | 8.3 | 7.7 | 7.5
22 | 8.1 | 7.3 | 7.4
23 | 7.5 | 6.2 | 7.3
0 | 6.9 | 5.9 | 7.2
1 | 4.7 | 6.3 | 6.7
2 | 3.6 | 6.1 | 6.1
3 | 2.6 | 5.9 | 5.5
4 | 2.7 | 5.8 | 5.8
5 | 2.8 | 5.7 | 6.2
6 | 3.2 | 5.5 | 5.8
7 | 2.7 | 4.8 | 5.9
8 | 3.1 | 6 | 5.8
9 | 3.7 | 7.2 | 7.4
10 | 5.2 | 8.6 | 8.1
11 | 5.2 | 9.8 | 8.6
12 | 5.5 | 10.6 | 9.4
13 | 5.6 | 10.5 | 9.6
14 | 5.7 | 10.8 | 9.8
15 | 5.8 | 10.4 | 9.4
16 | 6.2 | 10.6 | 9.8
17 | 6.2 | 10.1 | 9.4
18 | 4.8 | 9.2 | 8.7
19 | 5.3 | 8.3 | 7.8
20 | 4.8 | 7.7 | 7.9
21 | 3.6 | 7.4 | 7.7
22 | 3.6 | 7.1 | 6.6
23 | 4.3 | 6.1 | 6.3
0 | 5.1 | 3.6 | 5.9
1 | 5.3 | 4.1 | 4.5
2 | 5.4 | 3.8 | 3.2
3 | 6 | 3.6 | 3.9
4 | 5.3 | 3.4 | 3.3
5 | 5.2 | 3.3 | 2.7
6 | 5.1 | 3.1 | 3.2
7 | 5.4 | 2.3 | 3.7
8 | 5.7 | 3.7 | 4
9 | 7 | 5.3 | 5.8
10 | 7.4 | 7.1 | 7.4
11 | 9 | 8.5 | 9
12 | 9.3 | 9.6 | 10.4
13 | 9.4 | 9.8 | 10.4
14 | 9.2 | 9.8 | 10.2
15 | 9.3 | 9.6 | 10.1
16 | 9.3 | 9.5 | 10.2
17 | 9.4 | 9 | 9.7
18 | 8.9 | 7.8 | 9
19 | 8 | 6.6 | 7.5
20 | 8.1 | 5.9 | 6.4
21 | 6.8 | 5.5 | 5.8
22 | 6.2 | 5.1 | 5.3
23 | 5.9 | 3.9 | 5.1
0 | 5.7 | 7.1 | 4.8
1 | 4.3 | 7.5 | 4
2 | 3.1 | 7.3 | 3.1
3 | 2.5 | 7.1 | 3.1
4 | 2.1 | 7 | 4.4
5 | 1.8 | 6.9 | 3.5
6 | 2.2 | 6.7 | 3.2
7 | 2.6 | 6 | 2.9
8 | 3.3 | 7.2 | 3.9
9 | 4.9 | 8.5 | 4.9
10 | 7.2 | 10 | 7.2
11 | 8.6 | 11.3 | 7.3
12 | 10 | 12.1 | 8.1
13 | 9.6 | 12.1 | 7.9
14 | 9.9 | 12.4 | 8.2
15 | 10.1 | 12.1 | 8.1
16 | 9.9 | 12 | 8.1
17 | 9.3 | 11.7 | 7.7
18 | 8.5 | 10.6 | 6.9
19 | 6.1 | 9.7 | 6
20 | 5.5 | 9.1 | 5.6
21 | 5.2 | 8.7 | 5.3
22 | 4.5 | 8.4 | 4.6
23 | 4.3 | 7.4 | 4.1
0 | 4.2 | 11.5 | 3.5
1 | 3.6 | 12 | 2.9
2 | 3.1 | 11.8 | 2.4
3 | 2.9 | 11.6 | 2
4 | 2.1 | 11.4 | 2.1
5 | 1.9 | 11.3 | 2.2
6 | 1.6 | 11.1 | 2
7 | 2.5 | 10.4 | 2.4
8 | 3.4 | 11.7 | 3.1
9 | 5.7 | 13 | 2.8
10 | 7.9 | 14.5 | 4.4
11 | 9.2 | 15.7 | 5.1
12 | 11.3 | 16.6 | 5.4
13 | 11.3 | 16.8 | 5.7
14 | 11.4 | 16.9 | 5.6
15 | 11.2 | 16.5 | 5.8
16 | 11 | 16.6 | 5.7
17 | 11.3 | 16.2 | 5.6
18 | 8.8 | 15.1 | 5.8
19 | 7.5 | 14.1 | 4.8
20 | 6.7 | 13.5 | 3.5
21 | 5.7 | 13.2 | 4
22 | 5.5 | 12.8 | 3.3
23 | 5.2 | 11.8 | 2.5
0 | 4.9 | 7.8 | 1.7
1 | 4.8 | 8.7 | 0.3
2 | 4.8 | 8.3 | -0.7
3 | 4.5 | 7.9 | -1.5
4 | 4.6 | 7.7 | -2.3
5 | 3.8 | 7.4 | -1.9
6 | 3.1 | 7 | -1.5
7 | 4.3 | 5.7 | -1.2
8 | 5.5 | 8.1 | -0.9
9 | 7.5 | 10.6 | 1
10 | 9.7 | 13.6 | 2.2
11 | 10.1 | 16 | 3.5
12 | 12.7 | 17.7 | 5.4
13 | 13 | 17.8 | 5.2
14 | 13.1 | 18.1 | 5.3
15 | 13 | 17.9 | 5.6
16 | 12.8 | 17.8 | 5.5
17 | 12.6 | 16.8 | 4.8
18 | 11 | 14.8 | 3.8
19 | 9.6 | 12.9 | 2.3
20 | 7.8 | 11.7 | 2.2
21 | 8.4 | 11 | 1.1
22 | 6.8 | 10.4 | 0.5
23 | 5.5 | 8.4 | 0.2
0 | 4.3 | 5 | -0.1
1 | 2.4 | 5.7 | -0.4
2 | 1 | 5.4 | -0.6
3 | -0.5 | 5 | -1.5
4 | -0.4 | 4.8 | -2.5
5 | -1.1 | 4.7 | -1.9
6 | -1.7 | 4.3 | -1.4
7 | 0 | 3.3 | -1.5
8 | 1.6 | 5.2 | -0.3
9 | 5.2 | 7.2 | 2.6
10 | 7.6 | 9.6 | 4.3
11 | 11.7 | 11.5 | 7
12 | 13.9 | 12.9 | 8.8
13 | 13.9 | 13 | 8.9
14 | 14 | 13.2 | 8.8
15 | 13.6 | 12.9 | 8.6
16 | 13.9 | 13.1 | 8.8
17 | 12.8 | 12.2 | 8.3
18 | 10.2 | 10.5 | 6.4
19 | 7.6 | 9 | 4.9
20 | 6.7 | 8.1 | 3.3
21 | 5.2 | 7.5 | 2.5
22 | 4.5 | 7 | 1.8
23 | 3.7 | 5.4 | 1.2
0 | 2.9 | 3.1 | 0.6
1 | 2.8 | 3.6 | 0.3
2 | 3 | 3.4 | 0
3 | 3.3 | 3.2 | -0.7
4 | 2 | 3 | -1.4
5 | 1.7 | 2.9 | -1.3
6 | 1.4 | 2.7 | -1.2
7 | 2.1 | 1.9 | -1.2
8 | 2.9 | 3.3 | -0.7
9 | 4.6 | 4.8 | 1.2
10 | 6.3 | 6.5 | 2.3
11 | 8.4 | 7.9 | 3.8
12 | 9.4 | 8.9 | 4.5
13 | 9.6 | 8.7 | 4.7
14 | 9.7 | 9.1 | 4.9
15 | 9.8 | 8.7 | 4.8
16 | 9.4 | 9.2 | 4.7
17 | 9.3 | 8.4 | 4.7
18 | 8.1 | 7.2 | 3.7
19 | 6.2 | 6.1 | 2
20 | 6.3 | 5.4 | 1.7
21 | 5.1 | 5 | 1.7
22 | 4.1 | 4.6 | 0.9
23 | 4.1 | 3.5 | 0.4
0 | 4.2 | 3.1 | -0.1
1 | 3.6 | 3.5 | -1
2 | 3.1 | 3.3 | -1.5
3 | 2.8 | 3.2 | -1.8
4 | 2.4 | 3 | -2.9
5 | 1.9 | 3 | -4.1
6 | 1.4 | 2.8 | -3.5
7 | 2.5 | 2.3 | -2.8
8 | 3.7 | 3.2 | -1.5
9 | 4.5 | 4.3 | 0.8
10 | 7.5 | 5.5 | 3.9
11 | 10 | 6.5 | 6.2
12 | 11.2 | 7.2 | 8.6
13 | 11.2 | 7.3 | 9
14 | 11.1 | 7.4 | 9.1
15 | 11.3 | 7.2 | 8.9
16 | 11 | 7.2 | 9
17 | 10.3 | 6.8 | 7.9
18 | 9.3 | 6 | 6.4
19 | 7.1 | 5.2 | 4.5
20 | 6.9 | 4.7 | 2.4
21 | 5.8 | 4.4 | 2.1
22 | 4.7 | 4.2 | 0.7
23 | 4.5 | 3.4 | 0.3
0 | 4.3 | 5 | -0.1
1 | 3.9 | 5.8 | 0.7
2 | 3.4 | 5.4 | 1.3
3 | 3.5 | 5.1 | -0.2
4 | 3.1 | 4.9 | 0
5 | 2.6 | 4.7 | 0.3
6 | 2.4 | 4.4 | -0.2
7 | 2.2 | 3.2 | -1
8 | 4.1 | 5.3 | 0.9
9 | 5.9 | 7.4 | 2.7
10 | 7.7 | 9.9 | 4.7
11 | 9.7 | 12 | 6.8
12 | 10.5 | 13.4 | 8
13 | 10.8 | 13.7 | 8.3
14 | 10.7 | 13.8 | 8.5
15 | 11 | 13.5 | 8.3
16 | 10.7 | 13.5 | 8.4
17 | 10.7 | 12.6 | 7.9
18 | 8.7 | 10.9 | 6
19 | 8.4 | 9.3 | 5.2
20 | 6.7 | 8.3 | 3.9
21 | 5.9 | 7.7 | 3.2
22 | 4.9 | 7.2 | 2.6
23 | 4.3 | 5.5 | 2.2
0 | 3.6 | 3.4 | 1.7
1 | 2.3 | 4.3 | 0.8
2 | 1.4 | 3.9 | 0
3 | 2.4 | 3.5 | -0.5
4 | 0.9 | 3.2 | -1.1
5 | 1.1 | 3 | -0.8
6 | 0.7 | 2.6 | -0.5
7 | 0.4 | 1.1 | -0.2
8 | 2.2 | 3.7 | 0.4
9 | 4.1 | 6.4 | 2
10 | 6 | 9.6 | 4.1
11 | 7.4 | 12.1 | 6.9
12 | 8.7 | 13.9 | 7.8
13 | 9.3 | 14.1 | 7.9
14 | 9.1 | 14.4 | 7.8
15 | 8.8 | 14.3 | 7.8
16 | 9.1 | 14.2 | 7.5
17 | 8.5 | 13 | 7.1
18 | 7.6 | 10.8 | 5.9
19 | 5.4 | 8.8 | 4.6
20 | 4.7 | 7.5 | 4.1
21 | 4.8 | 6.8 | 3.4
22 | 3.5 | 6.1 | 2.2
23 | 3 | 4 | 1.9
0 | 2.6 | 2.4 | 1.5
1 | 1.9 | 3.2 | 1.7
2 | 1.2 | 2.8 | 1.9
3 | 0.7 | 2.4 | 1.4
4 | 1.2 | 2.2 | 1
5 | 0.4 | 1.9 | 1.3
6 | -0.4 | 1.5 | 1.6
7 | 0.9 | 0.2 | 1.6
8 | 2.2 | 2.6 | 1.1
9 | 4.1 | 5.2 | 3.1
10 | 6.6 | 8.2 | 4.2
11 | 8.5 | 10.7 | 4.5
12 | 10.1 | 12.4 | 5.7
13 | 10.2 | 12.8 | 5.3
14 | 10.3 | 12.9 | 5.8
15 | 10.6 | 12.9 | 5.7
16 | 10.3 | 12.8 | 5.5
17 | 9.4 | 11.5 | 5.6
18 | 8.6 | 9.4 | 5.4
19 | 6.7 | 7.5 | 3.8
20 | 5.3 | 6.3 | 3.7
21 | 4.5 | 5.6 | 3.2
22 | 3.4 | 4.9 | 2.5
23 | 3.2 | 3 | 4.7
0 | 2.9 | 5.6 | 6.8
1 | 1.8 | 5.9 | 7.3
2 | 1.1 | 5.8 | 7.7
3 | -1.3 | 5.6 | 7.7
4 | -0.5 | 5.5 | 7.3
5 | -0.5 | 5.3 | 6.8
6 | -1.2 | 5.2 | 7.3
7 | -1.9 | 4.5 | 7.7
8 | 0.7 | 5.7 | 7.3
9 | 3.3 | 6.9 | 8.7
10 | 7.1 | 8.3 | 9.5
11 | 9.1 | 9.4 | 11.1
12 | 10.5 | 10.2 | 11.2
13 | 11.5 | 10.2 | 11.1
14 | 11.6 | 10.4 | 11.5
15 | 11.5 | 10.3 | 11.4
16 | 11.4 | 10.2 | 11.4
17 | 10.6 | 9.8 | 11.4
18 | 9 | 8.8 | 10.7
19 | 6.8 | 7.9 | 9.9
20 | 5 | 7.4 | 9.2
21 | 4 | 7.1 | 8.8
22 | 2.9 | 6.7 | 8
23 | 2.6 | 5.8 | 9.9
0 | 2.3 | 2.4 | 11.7
1 | 2.7 | 2.7 | 12
2 | 2.5 | 2.4 | 12.2
3 | 2.5 | 2.2 | 12.1
4 | 2.4 | 2.1 | 11.9
5 | 2.1 | 1.9 | 11.7
6 | 1.7 | 1.3 | 11.9
7 | 2.9 | 2.1 | 12.1
8 | 4 | 3.3 | 12
9 | 6 | 4.9 | 12.7
10 | 7.8 | 6.3 | 13.2
11 | 9.2 | 7.4 | 13.4
12 | 10 | 8.2 | 13.6
13 | 9.9 | 8.4 | 13.5
14 | 10.3 | 8.5 | 13.8
15 | 10.2 | 8.4 | 13.9
16 | 10.1 | 8.2 | 13.5
17 | 10.2 | 7.9 | 13.8
18 | 8.4 | 6.8 | 13.4
19 | 6.7 | 5.6 | 12.7
20 | 6.4 | 4.7 | 12.4
21 | 5.4 | 4.1 | 12.7
22 | 4 | 3.7 | 12.3
23 | 4.8 | 2.7 | 12.5
0 | 5.5 | 0.9 | 12.6
1 | 5.8 | 1.2 | 11.8
2 | 5.9 | 0.9 | 11.4
3 | 5.8 | 0.7 | 10.9
4 | 5.5 | 0.5 | 10.9
5 | 5.6 | 0.4 | 11
6 | 5.6 | -0.5 | 11.1
7 | 5.8 | 0.6 | 10.9
8 | 6.5 | 1.9 | 11.5
9 | 8.3 | 3.9 | 11.6
10 | 8.4 | 5.6 | 12.3
11 | 9.8 | 6.9 | 12.4
12 | 9.5 | 7.9 | 12.4
13 | 9.7 | 7.9 | 12.2
14 | 9.8 | 8.2 | 12
15 | 9.6 | 8 | 12
16 | 9.6 | 7.9 | 12.2
17 | 9.6 | 7.6 | 11.8
18 | 9.7 | 6.2 | 12.3
19 | 7.9 | 4.7 | 11.4
20 | 7.4 | 3.6 | 11.6
21 | 7.6 | 3 | 11.2
22 | 6.4 | 2.4 | 11.6
23 | 7 | 1.3 | 10.9
0 | 7.6 | 4.7 | 9.5
1 | 7.5 | 5 | 7.4
2 | 7.2 | 4.7 | 5.3
3 | 6.7 | 4.5 | 5.5
4 | 6.4 | 4.4 | 5.7
5 | 6 | 4.2 | 5.5
6 | 6.4 | 3.5 | 5.5
7 | 6.6 | 4.4 | 5.7
8 | 9.2 | 5.6 | 6.7
9 | 12.3 | 7.3 | 8
10 | 14.6 | 8.8 | 9.2
11 | 16 | 9.9 | 10.2
12 | 16.7 | 10.8 | 10.6
13 | 16.9 | 10.8 | 10.4
14 | 17.2 | 11.1 | 10.9
15 | 17.1 | 11 | 10.5
16 | 17.1 | 10.8 | 10.7
17 | 16.8 | 10.5 | 10.6
18 | 14.3 | 9.4 | 9.7
19 | 13.4 | 8.1 | 9.2
20 | 12 | 7.1 | 7.7
21 | 10.6 | 6.5 | 7.3
22 | 10 | 6.1 | 7.2
23 | 9.4 | 5 | 7.1
0 | 8.9 | 5.5 | 6.9
1 | 8.4 | 5.9 | 6.7
2 | 7.9 | 5.6 | 6.6
3 | 7.6 | 5.4 | 6.5
4 | 7.8 | 5.2 | 6
5 | 7.5 | 5.1 | 6
6 | 7.2 | 4.4 | 6
7 | 8.6 | 5.3 | 6.3
8 | 10 | 6.5 | 6.5
9 | 11.7 | 8.1 | 7.5
10 | 12.6 | 9.5 | 8.3
11 | 13.9 | 10.6 | 9.1
12 | 14.9 | 11.4 | 9.7
13 | 14.7 | 11.7 | 9.4
14 | 14.8 | 11.7 | 9.7
15 | 15.2 | 11.4 | 9.5
16 | 15.1 | 11.2 | 9.3
17 | 15.1 | 11.2 | 9.6
18 | 14.1 | 10.1 | 8.9
19 | 11.6 | 8.8 | 8.1
20 | 11.1 | 7.9 | 8.1
21 | 10.6 | 7.3 | 8
22 | 9.8 | 6.9 | 7.3
23 | 10 | 5.9 | 6.8
0 | 10.3 | 3.7 | 6.3
1 | 10.3 | 4.1 | 4.9
2 | 10.3 | 3.8 | 4
3 | 10.4 | 3.5 | 3
4 | 10.5 | 3.3 | 3.4
5 | 10.7 | 3.2 | 3.8
6 | 10.4 | 2.4 | 3.9
7 | 10.5 | 3.4 | 3.9
8 | 11.4 | 4.8 | 5.3
9 | 12.2 | 6.7 | 6.9
10 | 12.7 | 8.4 | 8.1
11 | 13.3 | 9.7 | 9.8
12 | 13.5 | 10.7 | 10.7
13 | 13.3 | 10.9 | 10.3
14 | 13.4 | 11.1 | 10.7
15 | 13.6 | 11 | 10.8
16 | 13.2 | 11 | 10.7
17 | 13.3 | 10.4 | 10.1
18 | 13.5 | 9.1 | 8.3
19 | 11.8 | 7.6 | 7.4
20 | 11.7 | 6.4 | 7.1
21 | 11.7 | 5.8 | 5.6
22 | 11.2 | 5.3 | 5
23 | 10.9 | 4.1 | 5.6
0 | 10.6 | 3.3 | 6.2
1 | 9.2 | 3.8 | 6.4
2 | 8 | 3.4 | 6.3
3 | 7.8 | 3 | 5
4 | 7.6 | 2.8 | 4.8
5 | 7.8 | 2.6 | 4.5
6 | 7.9 | 1.5 | 5.1
7 | 7.9 | 2.9 | 5.6
8 | 8.7 | 4.8 | 7.2
9 | 10.2 | 7.4 | 9
10 | 11.8 | 9.8 | 10.8
11 | 12.2 | 11.6 | 11.9
12 | 13.2 | 12.9 | 13.9
13 | 12.7 | 13.2 | 13.7
14 | 13.1 | 13.4 | 14.1
15 | 13.2 | 13.4 | 14
16 | 12.7 | 13.2 | 14
17 | 12.7 | 12.5 | 13.1
18 | 11.6 | 10.7 | 12.4
19 | 10.9 | 8.6 | 10.3
20 | 10.4 | 7.1 | 9.1
21 | 10.6 | 6.2 | 9.2
22 | 9.8 | 5.5 | 7.5
23 | 9.3 | 3.9 | 7.2
0 | 8.9 | 5.4 | 6.9
1 | 7.9 | 5.7 | 6.1
2 | 7 | 5.4 | 5.2
3 | 6.8 | 5.2 | 5.1
4 | 6.9 | 5.1 | 4.9
5 | 6.4 | 5 | 5.1
6 | 5.8 | 4.3 | 5.3
7 | 7.1 | 5.2 | 5.6
8 | 8.5 | 6.2 | 6
9 | 11.7 | 7.7 | 7.6
10 | 13.6 | 9 | 9.1
11 | 15.4 | 10 | 9.9
12 | 17 | 10.8 | 10.5
13 | 17.2 | 10.9 | 10.8
14 | 16.7 | 11.1 | 10.7
15 | 16.8 | 10.8 | 10.9
16 | 17 | 10.9 | 11
17 | 16.4 | 10.5 | 10.6
18 | 14.6 | 9.5 | 9.8
19 | 12.3 | 8.4 | 9.1
20 | 11.7 | 7.5 | 7.8
21 | 10.6 | 7 | 7.5
22 | 9.7 | 6.6 | 7.5
23 | 9.3 | 5.7 | 6.8
0 | 8.9 | 5.4 | 6.1
1 | 8.2 | 5.6 | 5.3
2 | 7.6 | 5.4 | 4.3
3 | 6.9 | 5.3 | 4
4 | 7.2 | 5.2 | 3.5
5 | 7.5 | 5.1 | 3.3
6 | 7.1 | 4.7 | 3
7 | 7.1 | 5.2 | 4.2
8 | 9.2 | 5.9 | 5.3
9 | 10.6 | 6.8 | 9
10 | 12.2 | 7.7 | 10.9
11 | 13.1 | 8.3 | 12.6
12 | 13.1 | 8.8 | 14.1
13 | 13.6 | 8.5 | 14.7
14 | 13.9 | 9 | 14.4
15 | 14 | 8.5 | 14.4
16 | 13.9 | 8.9 | 14.4
17 | 13.6 | 8.7 | 14.3
18 | 12.6 | 8 | 12.6
19 | 10.9 | 7.3 | 10.6
20 | 10 | 6.7 | 8.9
21 | 9.4 | 6.4 | 8.1
22 | 9.5 | 6.2 | 7.1
23 | 9.2 | 5.6 | 6.5
0 | 8.8 | 3.6 | 5.8
1 | 8.1 | 3.8 | 5.1
2 | 7.3 | 3.6 | 4.5
3 | 7.3 | 3.5 | 4.8
4 | 7.7 | 3.4 | 4.3
5 | 7.1 | 3.4 | 4.1
6 | 6.6 | 3 | 4
7 | 7.8 | 3.5 | 4.9
8 | 9 | 4.1 | 5.8
9 | 12.3 | 5 | 7.4
10 | 13.8 | 5.9 | 8.1
11 | 14.8 | 6.5 | 9.1
12 | 16.3 | 7 | 9.9
13 | 16.1 | 6.8 | 9.7
14 | 16 | 7.1 | 10.2
15 | 16.4 | 6.9 | 9.8
16 | 16.4 | 6.7 | 10.2
17 | 15.6 | 6.8 | 9.5
18 | 14.4 | 6.2 | 9.2
19 | 12.1 | 5.5 | 8
20 | 11.3 | 4.9 | 6.8
21 | 10.4 | 4.6 | 6.3
22 | 10.3 | 4.4 | 5.4
23 | 9.3 | 3.8 | 5.2
0 | 8.3 | 3.7 | 5
1 | 7.3 | 4 | 3.9
2 | 6.5 | 3.7 | 3.1
3 | 5.7 | 3.5 | 2.9
4 | 5.6 | 3.4 | 3
5 | 5.5 | 3.2 | 2.6
6 | 5.9 | 2.6 | 2.2
7 | 6.3 | 3.5 | 3
8 | 7.9 | 4.6 | 3.8
9 | 9.9 | 6.2 | 5.1
10 | 12.2 | 7.7 | 6.6
11 | 13.4 | 8.8 | 7.7
12 | 14.1 | 9.6 | 8.8
13 | 14.5 | 9.9 | 8.7
14 | 14.8 | 9.9 | 8.4
15 | 14.4 | 9.6 | 8.9
16 | 14.5 | 9.9 | 8.7
17 | 14.5 | 9.4 | 8.7
18 | 12.9 | 8.2 | 7.7
19 | 11.3 | 7 | 6.5
20 | 10.5 | 6 | 5.4
21 | 9.3 | 5.5 | 4.8
22 | 8.2 | 5 | 4.4
23 | 7.1 | 4 | 5.6
0 | 5.9 | 6 | 6.7
1 | 3.5 | 6.2 | 7.5
2 | 2 | 6.1 | 8.1
3 | 1.2 | 6 | 7.5
4 | 0.8 | 5.9 | 7.9
5 | 0.4 | 5.8 | 7.4
6 | 0.9 | 5.5 | 6.7
7 | 1.4 | 5.9 | 7.9
8 | 4.2 | 6.5 | 8.9
9 | 6.5 | 7.2 | 11
10 | 9.4 | 7.9 | 13
11 | 11.3 | 8.4 | 14.2
12 | 12.2 | 8.8 | 15.5
13 | 13.1 | 8.5 | 15.5
14 | 12.9 | 8.9 | 15.6
15 | 12.8 | 8.6 | 15.5
16 | 12.6 | 8.9 | 15.2
17 | 12.3 | 8.7 | 15.5
18 | 10.4 | 8.2 | 13.6
19 | 8.5 | 7.6 | 12.4
20 | 6.2 | 7.1 | 11.1
21 | 5.3 | 6.9 | 10.2
22 | 5 | 6.7 | 10.1
23 | 4.4 | 6.2 | 9.4
0 | 3.8 | 3.2 | 8.7
1 | 3.5 | 3.4 | 7.5
2 | 3 | 3.2 | 6.8
3 | 3.1 | 3.1 | 6
4 | 2.9 | 3 | 5.1
5 | 2.6 | 2.9 | 5.6
6 | 2.3 | 2.4 | 6.1
7 | 3.5 | 3 | 6.1
8 | 4.6 | 3.9 | 7.8
9 | 6.9 | 5.1 | 10.9
10 | 8.6 | 6.2 | 12.9
11 | 11 | 7 | 14.6
12 | 11.7 | 7.6 | 16.4
13 | 11.7 | 7.4 | 16.2
14 | 11.8 | 7.8 | 16.6
15 | 11.5 | 7.8 | 16.2
16 | 11.5 | 7.4 | 16.5
17 | 11.5 | 7.4 | 16.3
18 | 10.2 | 6.6 | 14.9
19 | 7.3 | 5.6 | 11.7
20 | 7.2 | 4.9 | 10
21 | 5.7 | 4.5 | 9.5
22 | 5.9 | 4.2 | 8.9
23 | 5.1 | 3.5 | 8
0 | 4.4 | 2.3 | 7.1
1 | 3.1 | 2.6 | 5.7
2 | 2 | 2.4 | 4.9
3 | 1.9 | 2.2 | 4.2
4 | 1.8 | 2 | 3.9
5 | 1.3 | 1.9 | 3.3
6 | 0.7 | 1.3 | 2.8
7 | 2.5 | 2.1 | 4.1
8 | 4.3 | 3.1 | 5.4
9 | 6.8 | 4.6 | 10
10 | 9.6 | 5.9 | 12.2
11 | 11.2 | 6.9 | 14.5
12 | 13.1 | 7.6 | 16.1
13 | 13.3 | 7.9 | 16.5
14 | 13.4 | 7.9 | 16.7
15 | 13 | 7.5 | 16.6
16 | 13 | 7.5 | 16.6
17 | 12 | 7.4 | 16.3
18 | 11.3 | 6.4 | 14.2
19 | 8.6 | 5.2 | 11.9
20 | 6.9 | 4.4 | 9.3
21 | 5.1 | 3.9 | 8.5
22 | 5.1 | 3.5 | 7.8
23 | 4 | 2.6 | 6.6
0 | 2.9 | 2 | 5.4
1 | 1.7 | 2.3 | 4.5
2 | 0.8 | 2.1 | 3.9
3 | 0.8 | 1.9 | 2.9
4 | 0.2 | 1.7 | 2
5 | -0.5 | 1.6 | 2.4
6 | 0.3 | 1 | 2.8
7 | 1 | 1.8 | 3.2
8 | 3.1 | 2.9 | 5.4
9 | 6.7 | 4.4 | 8.3
10 | 9.3 | 5.7 | 10.9
11 | 10.7 | 6.7 | 13.4
12 | 12.7 | 7.5 | 15.1
13 | 12.6 | 7.5 | 15.2
14 | 12.7 | 7.8 | 15.3
15 | 12.6 | 7.3 | 15.4
16 | 12.8 | 7.4 | 15.3
17 | 12.3 | 7.3 | 14.6
18 | 9.6 | 6.2 | 12.3
19 | 7.6 | 5 | 10.9
20 | 5.8 | 4.2 | 8.1
21 | 4.3 | 3.7 | 7.7
22 | 4 | 3.3 | 7.2
23 | 3.7 | 2.3 | 6.4
0 | 3.4 | 1.8 | 5.6
1 | 3.6 | 2.1 | 5.8
2 | 3.7 | 1.8 | 6
3 | 3.4 | 1.6 | 5
4 | 3.4 | 1.5 | 5
5 | 3.3 | 1.4 | 4.4
6 | 3.5 | 0.6 | 3.9
7 | 3.7 | 1.6 | 5.1
8 | 4.1 | 2.7 | 6.3
9 | 4.4 | 4.3 | 8.4
10 | 5.4 | 5.7 | 11.7
11 | 6.1 | 6.8 | 12.4
12 | 6.3 | 7.6 | 13.5
13 | 6.1 | 7.5 | 13.9
14 | 6 | 7.9 | 14.3
15 | 6.4 | 7.6 | 14
16 | 6 | 7.7 | 13.8
17 | 6.3 | 7.4 | 14
18 | 6.3 | 6.3 | 12.3
19 | 5.1 | 5 | 10.6
20 | 5.3 | 4.1 | 9
21 | 4.6 | 3.5 | 8
22 | 4.6 | 3.1 | 7.5
23 | 4.2 | 2.1 | 6.5
0 | 3.9 | 0.5 | 5.5
1 | 3.5 | 0.9 | 4.5
2 | 3.3 | 0.6 | 3.5
3 | 3.4 | 0.3 | 3.4
4 | 3.9 | 0.2 | 3.3
5 | 3.4 | 0 | 3.5
6 | 3.3 | -0.8 | 3.6
7 | 3.1 | 0.3 | 4.3
8 | 3.7 | 1.5 | 4.6
9 | 4.2 | 3.3 | 6.9
10 | 5.6 | 4.9 | 8.2
11 | 5.2 | 6.1 | 9
12 | 6.1 | 7.1 | 9.6
13 | 6.1 | 7.1 | 9.7
14 | 5.9 | 7.4 | 9.6
15 | 6.2 | 7 | 9.5
16 | 6.4 | 7.2 | 9.2
17 | 5.6 | 6.8 | 9.5
18 | 6.1 | 5.5 | 8.7
19 | 5.5 | 4.1 | 6.8
20 | 4.5 | 3.1 | 6.6
21 | 4.6 | 2.5 | 5.3
22 | 4 | 2 | 6.1
23 | 4.2 | 2.8 | 4.9
0 | 4.4 | 3.5 | 3.8
1 | 4.7 | 4.3 | 2.6
2 | 4.9 | 5.1 | 1.4
3 | 3.7 | 4.9 | 1.3
4 | 3.5 | 4.6 | 0.9
5 | 3.1 | 4 | 0.6
6 | 3.8 | 4.4 | 0.9
7 | 4.3 | 5.4 | 1.1
8 | 8.5 | 7.2 | 2.5
9 | 11.1 | 9.1 | 3.9
10 | 13.3 | 10.5 | 4.5
11 | 15.1 | 11.6 | 5.9
12 | 17.2 | 12.5 | 6.5
13 | 17.6 | 13.2 | 6.4
14 | 17.8 | 13.3 | 6.6
15 | 17.7 | 13 | 6.7
16 | 17.3 | 13.1 | 5.9
17 | 17.1 | 12.5 | 5.8
18 | 15.3 | 11.3 | 5.4
19 | 12.3 | 9.9 | 4.8
20 | 10.8 | 8.6 | 3.3
21 | 9.5 | 7.6 | 2.7
22 | 7.4 | 7 | 2.5
23 | 7.8 | 6.2 | 2.2
0 | 8.1 | 6.8 | 1.9
1 | 8.3 | 6.6 | 0.5
2 | 8.3 | 6.2 | -0.8
3 | 8.2 | 6 | -1.6
4 | 8 | 5.7 | -1.8
5 | 8.3 | 5 | -2
6 | 8.5 | 5.4 | -1.4
7 | 8.7 | 6.5 | -0.8
8 | 9.7 | 8.4 | 0.7
9 | 11.8 | 10.4 | 2.9
10 | 12.4 | 11.9 | 5.2
11 | 13 | 13.1 | 6.4
12 | 13.9 | 14 | 7.8
13 | 13.8 | 14.7 | 7.4
14 | 13.7 | 14.8 | 7.3
15 | 14.1 | 14.3 | 7.4
16 | 14 | 14.6 | 7.3
17 | 13.9 | 14 | 7.6
18 | 13.4 | 12.8 | 6.2
19 | 11.6 | 11.2 | 4.7
20 | 11 | 9.9 | 3
21 | 10.9 | 8.9 | 1.2
22 | 9.6 | 8.2 | 0.5
23 | 9.9 | 7.4 | 0.7
0 | 10.2 | 8.7 | 1
1 | 9.6 | 8.5 | 0.9
2 | 9 | 8.2 | 0.6
3 | 9 | 8 | 0.8
4 | 8.9 | 7.8 | 0.3
5 | 8.8 | 7.3 | -0.2
6 | 9 | 7.6 | 0.2
7 | 9.3 | 8.4 | 0.5
8 | 9.9 | 10 | 1.7
9 | 9.9 | 11.6 | 3.8
10 | 11 | 12.9 | 6
11 | 12 | 13.8 | 7
12 | 11.8 | 14.6 | 7.4
13 | 11.6 | 15.1 | 8.2
14 | 12.1 | 15.2 | 8.3
15 | 11.7 | 14.8 | 8.2
16 | 11.7 | 15.1 | 8.2
17 | 11.7 | 14.5 | 7.8
18 | 11.7 | 13.5 | 7.4
19 | 10.7 | 12.3 | 5.2
20 | 10.5 | 11.2 | 3.7
21 | 9.9 | 10.4 | 3.5
22 | 10 | 9.8 | 3.1
23 | 9 | 9.2 | 2.8
0 | 8.1 | 7.9 | 2.6
1 | 5.6 | 7.6 | 2.3
2 | 3.9 | 7.2 | 2.3
3 | 3.9 | 6.9 | 1.4
4 | 3.9 | 6.5 | 1.2
5 | 3.9 | 5.7 | 1.2
6 | 4.1 | 6.2 | 1.1
7 | 4.4 | 7.5 | 2.1
8 | 5.3 | 9.8 | 3.1
9 | 6.5 | 12.2 | 4.5
10 | 7.7 | 14 | 5.9
11 | 8.6 | 15.4 | 7.1
12 | 9.6 | 16.5 | 8.1
13 | 9.1 | 17.4 | 7.9
14 | 9.4 | 17.5 | 8.2
15 | 9.6 | 16.9 | 7.9
16 | 9.4 | 17.3 | 8.1
17 | 9.3 | 16.5 | 8
18 | 8.5 | 15 | 6.8
19 | 7.9 | 13.2 | 6.1
20 | 6.9 | 11.6 | 4.7
21 | 6.4 | 10.4 | 4.4
22 | 5.7 | 9.5 | 3.4
23 | 5.9 | 8.5 | 3.6
0 | 6.1 | 9.2 | 3.8
1 | 6.2 | 9 | 3.4
2 | 6.5 | 8.7 | 3.1
3 | 5.6 | 8.5 | 3.5
4 | 5.4 | 8.2 | 3.1
5 | 5.3 | 7.6 | 3
6 | 5.5 | 8 | 2.8
7 | 5.6 | 8.9 | 3.9
8 | 8.3 | 10.6 | 4.9
9 | 10.2 | 12.4 | 6.2
10 | 10.7 | 13.8 | 7.9
11 | 12.2 | 14.8 | 9.1
12 | 13 | 15.6 | 9.3
13 | 13.1 | 16.2 | 9.6
14 | 13 | 16.3 | 9.8
15 | 13.2 | 15.8 | 9.1
16 | 13 | 16.2 | 9.7
17 | 13.1 | 15.6 | 9.5
18 | 12.1 | 14.5 | 8.7
19 | 9 | 13.1 | 7.7
20 | 8.8 | 11.9 | 6.1
21 | 8.4 | 11 | 5.6
22 | 8.4 | 10.4 | 5.3
23 | 7.1 | 9.7 | 4.9
0 | 5.8 | 8.3 | 4.5
1 | 3.6 | 8.1 | 3.8
2 | 1.8 | 7.7 | 3.3
3 | 1.4 | 7.4 | 3
4 | 0.8 | 7.1 | 2.6
5 | 0.7 | 6.5 | 2.3
6 | 0.7 | 6.9 | 2.6
7 | 2.2 | 8 | 3
8 | 3.9 | 9.9 | 5.8
9 | 6.8 | 12 | 8.5
10 | 7.8 | 13.5 | 10.6
11 | 9.5 | 14.7 | 11
12 | 10.7 | 15.7 | 12
13 | 11.2 | 16.4 | 13.1
14 | 11 | 16.5 | 13.1
15 | 10.8 | 15.9 | 13.3
16 | 11.2 | 16.3 | 13.2
17 | 9.8 | 15.6 | 12.8
18 | 8.5 | 14.4 | 11.4
19 | 7.2 | 12.8 | 9.4
20 | 5.8 | 11.4 | 7.9
21 | 4.4 | 10.4 | 6.7
22 | 4.4 | 9.7 | 6.2
23 | 4 | 8.9 | 5.7
0 | 3.6 | 6.8 | 5.2
1 | 3 | 6.6 | 3.8
2 | 2.4 | 6.1 | 2.3
3 | 3.1 | 5.8 | 2
4 | 1.9 | 5.5 | 1.6
5 | 1.9 | 4.8 | 1.8
6 | 1.8 | 5.2 | 2.1
7 | 2.8 | 6.4 | 2.6
8 | 3.9 | 8.6 | 4.4
9 | 6.8 | 10.9 | 6.4
10 | 7.5 | 12.7 | 8.2
11 | 9 | 14 | 9.6
12 | 10 | 15.1 | 10.9
13 | 10.2 | 15.9 | 11.3
14 | 9.8 | 16 | 11.5
15 | 10 | 15.6 | 11.5
16 | 10.3 | 15.8 | 11.1
17 | 8.9 | 15 | 11.1
18 | 8.6 | 13.6 | 9.7
19 | 7.5 | 11.9 | 7.7
20 | 6.1 | 10.3 | 6.9
21 | 4.7 | 9.2 | 5.8
22 | 4.6 | 8.4 | 5.1
23 | 4.2 | 7.5 | 5.3
0 | 3.7 | 4.3 | 5.4
1 | 2 | 4 | 5.8
2 | 0.5 | 3.5 | 5.9
3 | -0.4 | 3.1 | 5.8
4 | 0.1 | 2.7 | 5.7
5 | -0.2 | 1.9 | 5.4
6 | -0.6 | 2.5 | 5
7 | 1.9 | 3.8 | 6.5
8 | 4.4 | 6.4 | 7.8
9 | 7 | 9 | 10.2
10 | 9.8 | 11.1 | 11.5
11 | 11.7 | 12.6 | 12.5
12 | 13.3 | 13.9 | 13.3
13 | 14 | 14.8 | 13.8
14 | 13.6 | 14.9 | 14.1
15 | 13.7 | 14.4 | 13.6
16 | 13.8 | 14.7 | 13.9
17 | 12.4 | 13.8 | 13.2
18 | 10.9 | 12.2 | 12.5
19 | 8.6 | 10.2 | 11.6
20 | 7 | 8.3 | 9.9
21 | 5.4 | 7 | 8.8
22 | 4.7 | 6.1 | 8.5
23 | 4.7 | 5 | 7.6
0 | 4.8 | 5.7 | 6.8
1 | 5.3 | 5.5 | 5.3
2 | 5.3 | 5.1 | 4.5
3 | 5 | 4.8 | 4.2
4 | 4 | 4.5 | 3.7
5 | 3.9 | 3.9 | 3.7
6 | 3.6 | 4.3 | 3.6
7 | 6.8 | 5.3 | 4.3
8 | 9.8 | 7.2 | 5
9 | 12.7 | 9.2 | 6.7
10 | 16.7 | 10.7 | 8.2
11 | 18.6 | 11.9 | 8.7
12 | 19.9 | 12.8 | 9.9
13 | 20.9 | 13.5 | 9.8
14 | 21 | 13.6 | 10
15 | 20.9 | 13.1 | 9.6
16 | 21 | 13.5 | 9.9
17 | 20.2 | 12.8 | 9.8
18 | 17.5 | 11.6 | 8.8
19 | 15.3 | 10.1 | 7.8
20 | 12.2 | 8.7 | 6.3
21 | 10.3 | 7.7 | 6.1
22 | 9.1 | 7 | 5.8
23 | 8.6 | 6.2 | 4.9
0 | 8.1 | 4.8 | 4
1 | 6.7 | 4.6 | 1.8
2 | 5.1 | 4.4 | 0.3
3 | 5.8 | 4.2 | -0.1
4 | 4.7 | 4 | -0.4
5 | 4.5 | 3.5 | -0.5
6 | 4.3 | 3.8 | -0.6
7 | 6.6 | 4.6 | 0.9
8 | 8.9 | 5.9 | 2.5
9 | 12.9 | 7.3 | 4.7
10 | 14.6 | 8.3 | 7.3
11 | 16.7 | 9.1 | 8.2
12 | 18.3 | 9.8 | 9.2
13 | 19.1 | 10.3 | 9.6
14 | 19.1 | 10.4 | 10.1
15 | 19.3 | 9.8 | 9.6
16 | 19.3 | 10.2 | 9.7
17 | 18.3 | 9.8 | 8.9
18 | 15.9 | 8.9 | 7.6
19 | 13.7 | 7.9 | 6.7
20 | 12.6 | 6.9 | 4.8
21 | 10.9 | 6.2 | 4.2
22 | 8.8 | 5.7 | 3.1
23 | 9 | 5.2 | 2.7
0 | 9.2 | 5.6 | 2.4
1 | 8.6 | 5.4 | 1.7
2 | 7.9 | 5 | 0.9
3 | 7.4 | 4.7 | 0.7
4 | 7.5 | 4.5 | 0.6
5 | 7.3 | 3.9 | 0.9
6 | 7 | 4.3 | 1.1
7 | 8.8 | 5.3 | 1.8
8 | 10.6 | 7 | 2.7
9 | 14.1 | 9 | 5.1
10 | 15.5 | 10.4 | 6.7
11 | 17.3 | 11.5 | 8.1
12 | 18.2 | 12.4 | 8.7
13 | 18.7 | 13.1 | 8.6
14 | 19 | 13.2 | 8.7
15 | 19 | 12.7 | 9.1
16 | 18.8 | 13 | 8.6
17 | 18.3 | 12.4 | 8.5
18 | 17 | 11.2 | 8.2
19 | 15.1 | 9.8 | 5.9
20 | 13.4 | 8.5 | 5
21 | 11.9 | 7.5 | 4
22 | 11 | 6.9 | 4.1
23 | 10.8 | 6.1 | 4
0 | 10.6 | 7.6 | 3.9
1 | 9.5 | 7.4 | 4.3
2 | 8.7 | 7.1 | 4.4
3 | 7.9 | 6.9 | 4.5
4 | 7.4 | 6.7 | 4.4
5 | 7.4 | 6.2 | 4.2
6 | 7.4 | 6.5 | 3.8
7 | 9.2 | 7.3 | 5.3
8 | 11.1 | 8.7 | 6.7
9 | 13.2 | 10.2 | 9
10 | 15.1 | 11.4 | 10.1
11 | 17 | 12.2 | 11.4
12 | 17.9 | 13 | 12.3
13 | 18.2 | 13.5 | 12.6
14 | 18.4 | 13.6 | 12.8
15 | 18.6 | 13.2 | 12.7
16 | 18.2 | 13.4 | 12.4
17 | 17.6 | 12.9 | 11.8
18 | 16.2 | 12 | 11.6
19 | 14.9 | 10.9 | 9.8
20 | 13.3 | 9.8 | 8.8
21 | 11.8 | 9.1 | 7.8
22 | 11.4 | 8.6 | 6.1
23 | 11.6 | 8 | 6.2
0 | 11.9 | 3.1 | 6.3
1 | 12.2 | 2.7 | 5.7
2 | 12.4 | 2.1 | 5
3 | 12.4 | 1.7 | 5.1
4 | 12.1 | 1.2 | 4.7
5 | 12 | 0.3 | 4.5
6 | 11.9 | 0.9 | 4.4
7 | 12.9 | 2.5 | 5.6
8 | 13.9 | 5.5 | 6.8
9 | 14.9 | 8.6 | 8.3
10 | 15.7 | 11 | 10.3
11 | 16.7 | 12.8 | 11.8
12 | 16.9 | 14.3 | 12.7
13 | 16.8 | 15.4 | 12.7
14 | 17.2 | 15.5 | 12.9
15 | 16.8 | 15.4 | 12.6
16 | 17.1 | 15.2 | 12.7
17 | 17.1 | 14.2 | 12.2
18 | 15.8 | 12.3 | 12
19 | 15.3 | 9.9 | 9.9
20 | 14.1 | 7.8 | 8.7
21 | 13.5 | 6.3 | 7.5
22 | 13.5 | 5.2 | 7.5
23 | 12.5 | 3.9 | 6.7
0 | 11.5 | 2.1 | 5.9
1 | 8.7 | 1.9 | 4.4
2 | 6.9 | 1.5 | 3.5
3 | 6.5 | 1.2 | 1.7
4 | 6.3 | 0.9 | 1.7
5 | 6.2 | 0.2 | 1.6
6 | 6.2 | 0.7 | 1.5
7 | 6.2 | 1.8 | 3.2
8 | 9.2 | 3.8 | 5
9 | 11.3 | 5.9 | 6.8
10 | 12.6 | 7.5 | 9.1
11 | 14.2 | 8.7 | 10.7
12 | 15.3 | 9.7 | 12.3
13 | 15 | 10.5 | 12.2
14 | 15.6 | 10.6 | 12.3
15 | 15 | 10.2 | 12
16 | 15.3 | 10.4 | 12.6
17 | 15.1 | 9.7 | 12
18 | 13.9 | 8.4 | 10.5
19 | 12.2 | 6.8 | 8.5
20 | 11.1 | 5.3 | 6.6
21 | 9.8 | 4.3 | 5.9
22 | 8.7 | 3.6 | 4.7
23 | 8.7 | 2.7 | 5.1
0 | 8.7 | 4.3 | 5.6
1 | 7.9 | 4.1 | 5.4
2 | 7.3 | 3.8 | 5.3
3 | 7.1 | 3.6 | 4.4
4 | 6.9 | 3.3 | 4.1
5 | 6.7 | 2.8 | 3.8
6 | 6.9 | 3.1 | 4.6
7 | 7.1 | 4 | 5.3
8 | 9.3 | 5.6 | 7.8
9 | 9.7 | 7.2 | 10.4
10 | 11.9 | 8.5 | 12.5
11 | 12 | 9.5 | 14.1
12 | 13 | 10.3 | 15.3
13 | 13.2 | 10.9 | 16
14 | 12.6 | 10.9 | 16.4
15 | 13 | 10.4 | 16.5
16 | 12.9 | 10.8 | 16.4
17 | 13.1 | 10.2 | 16.4
18 | 12.9 | 9.2 | 14.2
19 | 10.7 | 8 | 11.8
20 | 9.6 | 6.8 | 10
21 | 8.9 | 6 | 9.2
22 | 8.5 | 5.4 | 8.1
23 | 8 | 4.7 | 9
0 | 7.5 | 3.8 | 9.8
1 | 6.7 | 3.4 | 9.9
2 | 6.4 | 3 | 10
3 | 4.8 | 2.8 | 9.9
4 | 4.7 | 2.3 | 9.8
5 | 4.7 | 1.9 | 10
6 | 5.5 | 2.7 | 10.2
7 | 6.3 | 4.3 | 10.2
8 | 8.5 | 6.4 | 11.7
9 | 10.1 | 8.2 | 12.7
10 | 12.3 | 9.7 | 13.7
11 | 13.6 | 11 | 14.6
12 | 14.6 | 12.1 | 14.5
13 | 14.4 | 12.8 | 14.7
14 | 15 | 12.7 | 15
15 | 14.5 | 13.1 | 14.6
16 | 14.6 | 12.8 | 14.7
17 | 13.6 | 12.2 | 14.7
18 | 13.5 | 11.1 | 14.4
19 | 11.3 | 9.5 | 13.9
20 | 9.9 | 7.7 | 12.2
21 | 8.7 | 6.3 | 11.6
22 | 7.1 | 5.4 | 10.7
23 | 7 | 4.6 | 10.2
0 | 6.8 | 8.8 | 9.8
1 | 5 | 8.4 | 6.5
2 | 3.5 | 8.1 | 4.1
3 | 3.5 | 7.9 | 4.2
4 | 3.4 | 7.5 | 4.1
5 | 3.5 | 7.2 | 4
6 | 3.7 | 7.8 | 4
7 | 5.5 | 9.1 | 6.5
8 | 7.9 | 10.8 | 9.2
9 | 9.9 | 12.4 | 12.2
10 | 10.7 | 13.6 | 14.3
11 | 13 | 14.7 | 15.3
12 | 13.9 | 15.6 | 17.4
13 | 14.2 | 16.2 | 17.9
14 | 14.1 | 16.2 | 18.2
15 | 13.9 | 16.4 | 17.6
16 | 14.4 | 16.2 | 17.5
17 | 13.7 | 15.7 | 17.7
18 | 12.2 | 14.7 | 15.9
19 | 11.4 | 13.4 | 13.8
20 | 9 | 12 | 11.2
21 | 7.8 | 10.8 | 8.9
22 | 6.1 | 10.1 | 8.8
23 | 6.9 | 9.4 | 8.5
0 | 7.7 | 9.8 | 8.2
1 | 7.1 | 9.3 | 7.7
2 | 6.4 | 9 | 7.6
3 | 6.1 | 8.7 | 7.1
4 | 6 | 8.2 | 6.6
5 | 5.9 | 7.8 | 6.8
6 | 6.5 | 8.6 | 7
7 | 7 | 10.3 | 7.9
8 | 8.5 | 12.4 | 9.3
9 | 10.3 | 14.3 | 10.8
10 | 10.4 | 15.9 | 11.6
11 | 11.7 | 17.2 | 12.3
12 | 12.4 | 18.3 | 14.1
13 | 12.6 | 19.1 | 14.2
14 | 12.4 | 19 | 14.5
15 | 12.9 | 19.4 | 14.4
16 | 12.7 | 19.1 | 14
17 | 12.3 | 18.4 | 14.1
18 | 11.4 | 17.3 | 13.6
19 | 10.5 | 15.6 | 12.3
20 | 9.7 | 13.8 | 11.2
21 | 9 | 12.4 | 9.8
22 | 7.8 | 11.4 | 9.2
23 | 7.5 | 10.6 | 8.2
0 | 7.1 | 9.5 | 7.2
1 | 5.1 | 9.1 | 5.7
2 | 3.8 | 8.9 | 4.5
3 | 4.4 | 8.7 | 3.8
4 | 4 | 8.3 | 3.6
5 | 3.8 | 8 | 3.5
6 | 4.6 | 8.6 | 4.7
7 | 5.5 | 9.9 | 6
8 | 6.8 | 11.6 | 8.6
9 | 9 | 13.1 | 11
10 | 10.7 | 14.4 | 13.4
11 | 10.1 | 15.4 | 14.1
12 | 12 | 16.3 | 15.3
13 | 12 | 16.9 | 16.8
14 | 11.9 | 16.5 | 17.1
15 | 12 | 17.1 | 17.1
16 | 12.6 | 16.9 | 17.1
17 | 12.5 | 16.4 | 15.2
18 | 10.2 | 15.4 | 14.8
19 | 10.2 | 14.1 | 13.2
20 | 8.7 | 12.7 | 10.6
21 | 7.4 | 11.6 | 9.4
22 | 6 | 10.8 | 7.8
23 | 6.2 | 10.2 | 7.9
0 | 6.3 | 8.3 | 8
1 | 6.2 | 7.8 | 8
2 | 6.1 | 7.5 | 7.8
3 | 5.5 | 7.3 | 8.1
4 | 5.4 | 6.8 | 7.9
5 | 5.4 | 6.4 | 7.7
6 | 6.4 | 7.2 | 7.9
7 | 7.3 | 8.8 | 8.2
8 | 9.7 | 10.8 | 9.2
9 | 10.1 | 12.7 | 10.1
10 | 12.4 | 14.2 | 10.9
11 | 13.7 | 15.5 | 11.5
12 | 14.3 | 16.5 | 11.9
13 | 15.3 | 17.3 | 12.1
14 | 15.1 | 17.2 | 11.9
15 | 15 | 17.6 | 11.6
16 | 15.4 | 17.3 | 11.6
17 | 15 | 16.6 | 11.9
18 | 13.9 | 15.5 | 10.5
19 | 12.2 | 13.9 | 10.8
20 | 11.6 | 12.2 | 9.9
21 | 9.3 | 10.8 | 8.6
22 | 8.5 | 9.9 | 9.2
23 | 8.1 | 9.1 | 9.5
0 | 7.7 | 9.7 | 9.7
1 | 6.1 | 9.3 | 8.8
2 | 5 | 9.1 | 8.1
3 | 4.7 | 8.8 | 8.1
4 | 4.6 | 8.5 | 8
5 | 4.5 | 8.2 | 7.8
6 | 5.6 | 8.8 | 7.7
7 | 6.8 | 10.1 | 8.3
8 | 7.6 | 11.8 | 8.9
9 | 9.9 | 13.3 | 10.8
10 | 12.2 | 14.5 | 12.2
11 | 12.5 | 15.6 | 11.9
12 | 14.1 | 16.5 | 12.5
13 | 14.7 | 17.1 | 12.5
14 | 13.8 | 17 | 12.6
15 | 13.6 | 17.3 | 11.6
16 | 14.2 | 17.1 | 12.9
17 | 14.6 | 16.6 | 12.6
18 | 12.5 | 15.6 | 12.1
19 | 11.6 | 14.3 | 11
20 | 10 | 12.9 | 10.5
21 | 8.9 | 11.8 | 9.1
22 | 8.1 | 11 | 9.5
23 | 7.1 | 10.3 | 9.3
0 | 6.1 | 8.7 | 9
1 | 3.8 | 8.3 | 7.7
2 | 2.4 | 8.1 | 6.9
3 | 2 | 7.8 | 7
4 | 1.7 | 7.5 | 6.5
5 | 1.8 | 7.2 | 6.1
6 | 2.1 | 7.8 | 6.5
7 | 3.7 | 9.1 | 6.9
8 | 6 | 10.8 | 8.9
9 | 7.9 | 12.3 | 10.5
10 | 9.3 | 13.5 | 12.9
11 | 10 | 14.6 | 12.9
12 | 11.4 | 15.4 | 13.7
13 | 12.2 | 16.1 | 13.3
14 | 12.2 | 16.1 | 13.5
15 | 11.6 | 16.3 | 13.1
16 | 11.8 | 16.1 | 14.2
17 | 11 | 15.6 | 14
18 | 10.1 | 14.6 | 12.6
19 | 8.3 | 13.3 | 11.1
20 | 6.7 | 11.9 | 10.2
21 | 5.7 | 10.7 | 9.3
22 | 4.3 | 10 | 8.9
23 | 5 | 9.3 | 8.3
0 | 5.7 | 4.2 | 7.6
1 | 6.3 | 3.6 | 6.4
2 | 6.3 | 3.3 | 5.7
3 | 6.2 | 3 | 5.7
4 | 6 | 2.5 | 5.6
5 | 5.7 | 2.1 | 5.6
6 | 6.2 | 2.9 | 6.2
7 | 6.5 | 4.6 | 6.8
8 | 9.1 | 6.8 | 9.5
9 | 10.3 | 8.8 | 11.4
10 | 12.6 | 10.5 | 12.9
11 | 13.7 | 11.8 | 13.6
12 | 13.9 | 13 | 15.2
13 | 14 | 13.8 | 15.3
14 | 13.6 | 13.7 | 15.5
15 | 14.1 | 14.1 | 14.9
16 | 14 | 13.8 | 14.9
17 | 13.8 | 13.1 | 15.4
18 | 12.5 | 11.9 | 14.2
19 | 10.2 | 10.2 | 13.4
20 | 10.2 | 8.3 | 11.2
21 | 8.7 | 6.8 | 9.6
22 | 8.9 | 5.9 | 8.4
23 | 8.1 | 5 | 8.2
0 | 7.4 | 6.4 | 8
1 | 5.9 | 5.8 | 7.1
2 | 5 | 5.4 | 6.5
3 | 4.8 | 5 | 5.8
4 | 4.6 | 4.4 | 5.8
5 | 4.7 | 3.9 | 5.8
6 | 4.7 | 4.9 | 6.3
7 | 5.6 | 7 | 6.9
8 | 6.6 | 9.7 | 8.4
9 | 8.4 | 12.2 | 11.3
10 | 10.6 | 14.2 | 12.3
11 | 10.1 | 15.9 | 13.3
12 | 10.9 | 17.3 | 13.3
13 | 10.6 | 18.3 | 14.2
14 | 10.3 | 18.5 | 14.5
15 | 11.3 | 18.7 | 14.1
16 | 10.5 | 18.3 | 14.4
17 | 10.9 | 17.4 | 13.9
18 | 9.5 | 15.9 | 12.8
19 | 10 | 13.8 | 11.5
20 | 8.3 | 11.5 | 11
21 | 7.1 | 9.7 | 9.3
22 | 6.1 | 8.5 | 9
23 | 6.8 | 7.4 | 7.9
0 | 7.5 | 6.5 | 6.7
1 | 7.3 | 6.1 | 4.7
2 | 7.2 | 5.9 | 3.4
3 | 7.6 | 5.7 | 2.2
4 | 7.3 | 5.3 | 2
5 | 7.1 | 5 | 1.9
6 | 6.9 | 5.6 | 2.8
7 | 8.4 | 6.9 | 3.8
8 | 10 | 8.5 | 7.7
9 | 12.1 | 10 | 9.9
10 | 11.6 | 11.2 | 13.3
11 | 13.5 | 12.3 | 14.5
12 | 13.4 | 13.1 | 16.6
13 | 14.3 | 13.7 | 17.7
14 | 14 | 13.7 | 18
15 | 14.4 | 13.9 | 17.3
16 | 14.2 | 13.7 | 17.6
17 | 14.1 | 13.2 | 17.7
18 | 14.3 | 12.3 | 15.2
19 | 11.6 | 11 | 13.4
20 | 10.6 | 9.6 | 10.3
21 | 9.7 | 8.5 | 9
22 | 9.6 | 7.8 | 6.9
23 | 9 | 7.1 | 7
0 | 8.3 | 6.8 | 7.2
1 | 7.2 | 6.5 | 7.5
2 | 6.6 | 6.4 | 7.5
3 | 6.1 | 6.3 | 7.5
4 | 5.6 | 6 | 7.4
5 | 5.7 | 5.8 | 7.3
6 | 5.9 | 6.2 | 7.1
7 | 7.8 | 7 | 8.8
8 | 10 | 8 | 10.6
9 | 11.9 | 8.9 | 11.8
10 | 13.6 | 9.7 | 13.4
11 | 14.6 | 10.3 | 14.2
12 | 15.4 | 10.8 | 15.4
13 | 16.5 | 11.2 | 16.1
14 | 15.9 | 11.1 | 15.6
15 | 15.9 | 11.4 | 16.2
16 | 15.9 | 11.2 | 16.1
17 | 16.1 | 10.9 | 16.1
18 | 14.4 | 10.3 | 14.9
19 | 12.8 | 9.6 | 14.1
20 | 10.8 | 8.7 | 12.1
21 | 9.2 | 8 | 11.3
22 | 9.3 | 7.6 | 9.2
23 | 9.3 | 7.2 | 10.4
0 | 9.2 | 6 | 11.6
1 | 8.8 | 5.6 | 11.5
2 | 8.6 | 5.3 | 11.5
3 | 7.5 | 5.1 | 11.5
4 | 7.4 | 4.7 | 11.5
5 | 7.2 | 4.4 | 11.6
6 | 8.3 | 5 | 11.5
7 | 9.4 | 6.4 | 11.4
8 | 12.7 | 8.2 | 11.5
9 | 14.8 | 9.8 | 11.5
10 | 16.6 | 11.1 | 11.5
11 | 17.4 | 12.2 | 11.6
12 | 19.6 | 13.1 | 11.5
13 | 20.5 | 13.7 | 11.5
14 | 20.8 | 13.6 | 11.4
15 | 20.4 | 14 | 11.4
16 | 20.3 | 13.8 | 11.5
17 | 20.2 | 13.2 | 11.4
18 | 19 | 12.2 | 11.5
19 | 16.4 | 10.9 | 11.4
20 | 14.9 | 9.4 | 11.4
21 | 13.4 | 8.2 | 11.4
22 | 11.5 | 7.4 | 11.5
23 | 10.4 | 6.7 | 11.6
0 | 9.3 | 1.1 | 9.7
1 | 6.7 | 0.5 | 8
2 | 5.1 | 0.1 | 6.7
3 | 4.1 | -0.3 | 6.6
4 | 4 | -0.8 | 6.5
5 | 3.9 | -1.3 | 6.7
6 | 5.3 | -0.4 | 6.9
7 | 6.8 | 1.6 | 7.9
8 | 8.8 | 4.2 | 8.9
9 | 11.8 | 6.5 | 11.1
10 | 14.6 | 8.4 | 12
11 | 15.9 | 9.9 | 13.7
12 | 17.7 | 11.2 | 14.4
13 | 17.8 | 12.1 | 15.1
14 | 18.4 | 12.1 | 14.6
15 | 17.8 | 12.5 | 14.6
16 | 17.7 | 12.2 | 14.6
17 | 17.5 | 11.4 | 14.9
18 | 16 | 10 | 13.9
19 | 12.9 | 8 | 12.5
20 | 11.3 | 5.9 | 11
21 | 9.3 | 4.1 | 10.2
22 | 7.6 | 3 | 8.8
23 | 8 | 2 | 9.5
0 | 8.5 | 3.1 | 10.3
1 | 8.5 | 2.6 | 10.4
2 | 8.2 | 2.3 | 10.4
3 | 8.4 | 2 | 10.6
4 | 8.4 | 1.6 | 10.4
5 | 8.2 | 1.2 | 10.3
6 | 7.9 | 2 | 10.4
7 | 9.7 | 3.6 | 10.5
8 | 11.4 | 5.6 | 12.8
9 | 14.3 | 7.5 | 13.9
10 | 15 | 9 | 15.3
11 | 17.2 | 10.3 | 16.3
12 | 17.7 | 11.3 | 16.4
13 | 17.9 | 12.1 | 16.5
14 | 17.3 | 12.1 | 16.3
15 | 18.1 | 12.4 | 16.8
16 | 17.6 | 12.1 | 16.5
17 | 17.8 | 11.4 | 16.6
18 | 16.8 | 10.3 | 16.4
19 | 14.8 | 8.7 | 15.1
20 | 13 | 7 | 13.8
21 | 11.9 | 5.6 | 12.8
22 | 11.2 | 4.7 | 11.9
23 | 10.8 | 3.9 | 11.5
0 | 10.3 | 4.1 | 11.1
1 | 8.5 | 3.7 | 9.6
2 | 7.3 | 3.4 | 8.3
3 | 7.1 | 3.2 | 8.4
4 | 6.8 | 2.8 | 8.3
5 | 6.6 | 2.5 | 8.2
6 | 7.6 | 3.1 | 9.7
7 | 8.7 | 4.5 | 11.2
8 | 11 | 6.3 | 13.5
9 | 12.9 | 7.9 | 15.9
10 | 14.3 | 9.3 | 18.5
11 | 16 | 10.4 | 21.5
12 | 16.7 | 11.3 | 21.4
13 | 18 | 12 | 22
14 | 17.5 | 11.8 | 22.6
15 | 17.7 | 12.2 | 22.7
16 | 18.1 | 12 | 22.2
17 | 17.7 | 11.4 | 21.8
18 | 16.5 | 10.4 | 21
19 | 14.5 | 9 | 17.7
20 | 12.7 | 7.5 | 16.7
21 | 11.4 | 6.3 | 14.3
22 | 9.9 | 5.5 | 12.6
23 | 10 | 5.9 | 10.5
0 | 10.2 | 6.3 | 8.5
1 | 10.4 | 6.8 | 6.4
2 | 10.5 | 7.2 | 4.3
3 | 10.4 | 6.9 | 4.2
4 | 10.2 | 6.5 | 4.1
5 | 10.1 | 6.6 | 4
6 | 11.1 | 7.4 | 5.1
7 | 12.2 | 8.6 | 6.2
8 | 13.9 | 9.9 | 9
9 | 16.3 | 11 | 12.4
10 | 17.7 | 12 | 13.6
11 | 18.9 | 12.8 | 15
12 | 19.8 | 13.5 | 17.1
13 | 19.8 | 13.9 | 17.7
14 | 20.4 | 14.2 | 18
15 | 20.3 | 14.2 | 17.8
16 | 20.4 | 13.9 | 17.9
17 | 19.9 | 13.5 | 17.8
18 | 18.9 | 12.8 | 16.9
19 | 16.9 | 11.8 | 14.4
20 | 15.1 | 10.6 | 11.4
21 | 13.7 | 9.5 | 8.2
22 | 12.4 | 8.8 | 7.9
23 | 11.3 | 8.3 | 7.7
0 | 10.2 | 8.6 | 7.6
1 | 6.7 | 8.1 | 5.5
2 | 4.3 | 7.8 | 3.9
3 | 4.1 | 7.4 | 3.5
4 | 4.1 | 7 | 3.2
5 | 4.1 | 7.1 | 3.4
6 | 4.2 | 8 | 3.7
7 | 5.9 | 9.5 | 5.3
8 | 8.2 | 11.1 | 8.1
9 | 9.6 | 12.4 | 9.9
10 | 10.9 | 13.5 | 11.4
11 | 12.6 | 14.5 | 12.8
12 | 12.5 | 15.3 | 14.6
13 | 13.6 | 15.9 | 15.2
14 | 14.2 | 16.1 | 14.9
15 | 14.2 | 16.2 | 15.3
16 | 13.6 | 15.9 | 14.5
17 | 13.3 | 15.3 | 15.3
18 | 12.1 | 14.5 | 12.9
19 | 10.6 | 13.3 | 12
20 | 9.3 | 11.8 | 9.4
21 | 7.4 | 10.6 | 7.4
22 | 6.9 | 9.7 | 6.5
23 | 7.1 | 9.2 | 6
0 | 7.3 | 8.4 | 5.5
1 | 6.7 | 7.7 | 3.9
2 | 6.3 | 7.3 | 2.8
3 | 5.9 | 6.8 | 3
4 | 5.8 | 6.2 | 2.8
5 | 5.7 | 6.3 | 2.7
6 | 7.1 | 7.6 | 3.6
7 | 8.4 | 9.7 | 4.5
8 | 9.5 | 11.9 | 6.8
9 | 11.1 | 13.8 | 8.5
10 | 12.8 | 15.4 | 10.3
11 | 13.1 | 16.8 | 11.9
12 | 14.8 | 17.9 | 11.5
13 | 14.5 | 18.6 | 11.9
14 | 15.2 | 19 | 12.3
15 | 14.9 | 19.2 | 11.6
16 | 14.7 | 18.7 | 11.8
17 | 15 | 17.9 | 11.4
18 | 13.6 | 16.7 | 10.1
19 | 12.8 | 15 | 9.2
20 | 10.4 | 13 | 7.9
21 | 8.7 | 11.2 | 6.3
22 | 8.4 | 10 | 5
23 | 8 | 9.2 | 5.5
0 | 7.5 | 7.7 | 6.1
1 | 6 | 6.9 | 6.2
2 | 4.9 | 6.4 | 6.2
3 | 4.7 | 5.9 | 6.1
4 | 4.7 | 5.3 | 6.4
5 | 5.2 | 5.4 | 6.7
6 | 5.8 | 6.7 | 6.5
7 | 6.4 | 9 | 7
8 | 8.9 | 11.4 | 8.9
9 | 10 | 13.4 | 10.1
10 | 10.5 | 15.1 | 10.9
11 | 11.7 | 16.6 | 11.5
12 | 13 | 17.8 | 12.6
13 | 13.7 | 18.6 | 12.8
14 | 13.8 | 19 | 12.4
15 | 13.5 | 19.1 | 12.6
16 | 13.4 | 18.6 | 12.9
17 | 13 | 17.7 | 12.7
18 | 12 | 16.5 | 12.3
19 | 11.1 | 14.7 | 11.2
20 | 9.3 | 12.5 | 9.3
21 | 7.3 | 10.6 | 9.1
22 | 7.3 | 9.4 | 8.5
23 | 7.4 | 8.5 | 8.4
0 | 7.4 | 9.8 | 8.2
1 | 6.5 | 9.3 | 7.7
2 | 5.9 | 8.9 | 7.2
3 | 5.8 | 8.6 | 7
4 | 5.8 | 8.1 | 6.8
5 | 6 | 8.2 | 6.8
6 | 6.3 | 9.2 | 6.8
7 | 8.1 | 10.8 | 9
8 | 10.1 | 12.5 | 10.9
9 | 12 | 14 | 12.5
10 | 13.2 | 15.2 | 14.1
11 | 14.2 | 16.3 | 15
12 | 14.9 | 17.2 | 15.7
13 | 15.3 | 17.7 | 16.6
14 | 15.8 | 18.1 | 16.5
15 | 15.4 | 18.1 | 16.9
16 | 15 | 17.7 | 16.4
17 | 15.6 | 17.1 | 17
18 | 14 | 16.2 | 15.7
19 | 12.1 | 14.9 | 13.8
20 | 11.5 | 13.4 | 12
21 | 9.9 | 12 | 11.1
22 | 7.9 | 11.1 | 10
23 | 7.6 | 10.5 | 10.2
0 | 7.2 | 10 | 10.5
1 | 4.9 | 9.3 | 10
2 | 3.8 | 8.9 | 9.8
3 | 2.6 | 8.4 | 9.7
4 | 2.6 | 7.8 | 9.4
5 | 2.6 | 8 | 9.1
6 | 3 | 9.2 | 10.4
7 | 6.8 | 11.2 | 11.7
8 | 9.3 | 13.4 | 13.8
9 | 11.8 | 15.2 | 16.2
10 | 14.1 | 16.8 | 17.8
11 | 16 | 18.1 | 20
12 | 17.4 | 19.2 | 20.7
13 | 16.9 | 19.9 | 21.7
14 | 18.5 | 20.3 | 21.7
15 | 18 | 20.4 | 21
16 | 18.2 | 19.9 | 21.4
17 | 17.4 | 19.2 | 21.7
18 | 17 | 18 | 19.9
19 | 13.4 | 16.4 | 18
20 | 10.3 | 14.4 | 16.2
21 | 8.1 | 12.7 | 14.2
22 | 7.4 | 11.6 | 13.2
23 | 7.1 | 10.8 | 12.2
0 | 6.8 | 9.4 | 11.2
1 | 5.9 | 9 | 9
2 | 5.1 | 8.8 | 7.2
3 | 4.9 | 8.5 | 6.7
4 | 4.8 | 8.2 | 6.7
5 | 4.7 | 8.3 | 6.7
6 | 6.4 | 8.9 | 7.6
7 | 8 | 10 | 8.7
8 | 10.5 | 11.2 | 9.9
9 | 13.2 | 12.1 | 11.1
10 | 15.6 | 13 | 12.9
11 | 16 | 13.7 | 13.6
12 | 18.3 | 14.3 | 14.1
13 | 19 | 14.6 | 15.3
14 | 19.5 | 14.9 | 14.8
15 | 19.1 | 14.9 | 14.9
16 | 19 | 14.7 | 14.8
17 | 18.4 | 14.2 | 14.9
18 | 17.5 | 13.6 | 12.8
19 | 15.3 | 12.8 | 12.4
20 | 12.5 | 11.7 | 11.3
21 | 9.9 | 10.8 | 9.8
22 | 9.5 | 10.2 | 9.4
23 | 9.4 | 9.8 | 8.6
0 | 9.3 | 9.4 | 7.9
1 | 7.7 | 9 | 5.9
2 | 6.7 | 8.7 | 4.5
3 | 5.8 | 8.5 | 4.6
4 | 5.8 | 8.1 | 4.3
5 | 5.8 | 8.2 | 4.2
6 | 6.6 | 8.9 | 4.9
7 | 8.4 | 10.1 | 5.8
8 | 11 | 11.3 | 8.2
9 | 12.3 | 12.3 | 9.5
10 | 13.8 | 13.2 | 10.9
11 | 15.9 | 13.9 | 12.7
12 | 16.7 | 14.5 | 13.3
13 | 16.9 | 15 | 13.6
14 | 17.7 | 15.2 | 13.8
15 | 17.1 | 15.2 | 14.2
16 | 17.6 | 15 | 14
17 | 17.1 | 14.5 | 13.7
18 | 15.7 | 13.9 | 13.3
19 | 14.1 | 13 | 11
20 | 11.5 | 11.9 | 9.2
21 | 10.1 | 10.9 | 7.8
22 | 9 | 10.3 | 7.3
23 | 9.9 | 9.8 | 7.4
0 | 10.7 | 8.6 | 7.4
1 | 10.8 | 8.2 | 7
2 | 10.5 | 7.9 | 6.3
3 | 10.5 | 7.7 | 6.2
4 | 10.4 | 7.3 | 6
5 | 10.4 | 7.4 | 5.9
6 | 11.6 | 8.1 | 6.6
7 | 12.7 | 9.4 | 7.3
8 | 14.4 | 10.6 | 9.8
9 | 15.7 | 11.7 | 11
10 | 17.3 | 12.7 | 12.3
11 | 18.9 | 13.5 | 13.2
12 | 19 | 14.1 | 13.4
13 | 19.3 | 14.6 | 14.3
14 | 18.9 | 14.8 | 14.2
15 | 18.7 | 14.9 | 14.6
16 | 18.9 | 14.6 | 14.1
17 | 18.9 | 14.1 | 13.8
18 | 16.9 | 13.4 | 13.1
19 | 16.1 | 12.4 | 11.7
20 | 14.6 | 11.3 | 10.5
21 | 13.6 | 10.2 | 9.6
22 | 12.2 | 9.6 | 8.2
23 | 12.2 | 9.1 | 8.4
0 | 12.1 | 7.1 | 8.5
1 | 10.7 | 6.4 | 8.1
2 | 9.7 | 6 | 7.9
3 | 9.6 | 5.5 | 7.8
4 | 9.5 | 4.9 | 7.7
5 | 9.7 | 5.1 | 7.6
6 | 9.9 | 6.2 | 8.2
7 | 11.9 | 8.3 | 8.8
8 | 14 | 10.4 | 10.5
9 | 14.8 | 12.2 | 11.5
10 | 16 | 13.7 | 12.8
11 | 17.8 | 15 | 13.7
12 | 19.2 | 16.1 | 13.6
13 | 18.8 | 16.8 | 14.6
14 | 19.2 | 17.2 | 14.7
15 | 19.1 | 17.3 | 14.2
16 | 19.4 | 16.8 | 14.2
17 | 18.1 | 16.1 | 14.4
18 | 17.8 | 14.9 | 13.6
19 | 15.8 | 13.3 | 12.8
20 | 14.4 | 11.4 | 11.4
21 | 13.3 | 9.7 | 10.6
22 | 12.2 | 8.6 | 9.9
23 | 12.1 | 7.8 | 9.7
0 | 12 | 5.3 | 9.5
1 | 10.8 | 4.6 | 8.7
2 | 9.9 | 4.1 | 7.7
3 | 9 | 3.7 | 7.7
4 | 9 | 3.1 | 7.7
5 | 9 | 3.2 | 7.7
6 | 10.5 | 4.4 | 7.8
7 | 12.1 | 6.5 | 9.7
8 | 14.2 | 8.7 | 11.1
9 | 15.8 | 10.6 | 13.6
10 | 18.3 | 12.1 | 15.6
11 | 19.3 | 13.5 | 16.3
12 | 20.1 | 14.6 | 17.7
13 | 20.4 | 15.4 | 16.8
14 | 21.4 | 15.8 | 18
15 | 21 | 15.9 | 17.7
16 | 20.4 | 15.4 | 17.7
17 | 20.6 | 14.6 | 17.8
18 | 20.3 | 13.4 | 17
19 | 17.3 | 11.8 | 15
20 | 15.2 | 9.8 | 13.4
21 | 13.9 | 8 | 11.4
22 | 12 | 6.9 | 10.8
23 | 11.4 | 6.1 | 9
0 | 10.8 | 5.8 | 7.2
1 | 8.4 | 5.4 | 2.8
2 | 6.8 | 5.1 | -0.1
3 | 6.8 | 4.8 | -0.8
4 | 6.6 | 4.5 | -1.2
5 | 6.5 | 4.6 | -1
6 | 8 | 5.3 | -0.5
7 | 9.7 | 6.5 | 2.5
8 | 12.7 | 7.9 | 5.5
9 | 15.7 | 9 | 8.5
10 | 17.4 | 9.9 | 11
11 | 19.1 | 10.8 | 12.8
12 | 20.8 | 11.4 | 16
13 | 21.2 | 11.8 | 15.4
14 | 21.6 | 12.1 | 16.7
15 | 21.9 | 12.2 | 15.8
16 | 21.3 | 11.9 | 16.1
17 | 20.8 | 11.4 | 16.1
18 | 19 | 10.7 | 12.8
19 | 17.3 | 9.7 | 10.4
20 | 14.8 | 8.5 | 7.6
21 | 12.8 | 7.4 | 5.6
22 | 10.6 | 6.8 | 3.4
23 | 10.8 | 6.3 | 3.9
0 | 10.9 | 5.4 | 4.4
1 | 10.5 | 4.9 | 4.3
2 | 10.7 | 4.6 | 3.7
3 | 10.1 | 4.3 | 3.2
4 | 9.5 | 3.9 | 3.2
5 | 9.5 | 4 | 3.1
6 | 9.5 | 4.8 | 4.8
7 | 11.3 | 6.2 | 6.4
8 | 13.1 | 7.7 | 9
9 | 14.7 | 9 | 11.2
10 | 16 | 10 | 13.1
11 | 18.1 | 11 | 14.2
12 | 18.1 | 11.7 | 16
13 | 19 | 12.2 | 17.1
14 | 18.8 | 12.5 | 17.2
15 | 19.1 | 12.6 | 17
16 | 18.5 | 12.2 | 16.7
17 | 18.9 | 11.7 | 16.2
18 | 17.6 | 10.9 | 14.8
19 | 16.2 | 9.8 | 13.8
20 | 14.6 | 8.4 | 10.1
21 | 13.3 | 7.2 | 8.5
22 | 11.7 | 6.4 | 7.3
23 | 11.3 | 5.9 | 7.2
0 | 10.9 | 8.9 | 7.1
1 | 8.2 | 8.5 | 6.4
2 | 5.9 | 8.3 | 5.9
3 | 5.6 | 8.1 | 5.2
4 | 5.3 | 7.8 | 5
5 | 5.1 | 7.8 | 4.9
6 | 7.2 | 8.4 | 6
7 | 9.5 | 9.5 | 7
8 | 13.1 | 10.6 | 10.2
9 | 17.6 | 11.5 | 11.9
10 | 18.7 | 12.3 | 13.8
11 | 21.6 | 13 | 15.6
12 | 23.3 | 13.5 | 16.8
13 | 23.3 | 13.9 | 17.7
14 | 25.4 | 14.1 | 17.5
15 | 24.8 | 14.2 | 17.1
16 | 24.9 | 13.9 | 17.4
17 | 23.8 | 13.5 | 17
18 | 22.3 | 12.9 | 15.6
19 | 18.9 | 12.1 | 14.2
20 | 15.8 | 11.1 | 11.7
21 | 13 | 10.3 | 10.4
22 | 12 | 9.7 | 8.4
23 | 11.4 | 9.3 | 9.1
0 | 10.7 | 4.4 | 9.8
1 | 10.3 | 3.9 | 9.9
2 | 9.9 | 3.6 | 10
3 | 9.8 | 3.2 | 10
4 | 9.7 | 2.8 | 9.9
5 | 9.9 | 2.9 | 9.8
6 | 10.2 | 3.8 | 10
7 | 12.9 | 5.3 | 10.3
8 | 15.9 | 7 | 11.3
9 | 18.6 | 8.3 | 11.1
10 | 19.9 | 9.5 | 12
11 | 22 | 10.5 | 12.2
12 | 22.2 | 11.3 | 12.6
13 | 23.1 | 11.9 | 12.3
14 | 23.8 | 12.2 | 12.1
15 | 23.2 | 12.3 | 12.2
16 | 23.4 | 11.9 | 12.1
17 | 23.4 | 11.3 | 12.2
18 | 22.3 | 10.4 | 11.8
19 | 19.3 | 9.2 | 12.2
20 | 16.9 | 7.7 | 11.3
21 | 14.6 | 6.5 | 10.5
22 | 13.7 | 5.6 | 10.5
23 | 13.6 | 5 | 9.9
0 | 13.4 | 9.7 | 9.3
1 | 12.5 | 9.3 | 7
2 | 11.7 | 9.1 | 5.3
3 | 11.6 | 8.9 | 5.2
4 | 11.4 | 8.7 | 5.2
5 | 12 | 8.9 | 5.5
6 | 12.6 | 9.5 | 5.9
7 | 14.8 | 10.4 | 7.7
8 | 17 | 11.3 | 10
9 | 19.1 | 12 | 12.3
10 | 20.8 | 12.6 | 13.2
11 | 22.1 | 13.2 | 14.7
12 | 22.4 | 13.7 | 16.2
13 | 24.5 | 14 | 16.1
14 | 23.7 | 14.2 | 17.1
15 | 24.5 | 14.4 | 16.4
16 | 24 | 14.1 | 16.7
17 | 23.5 | 13.8 | 15.8
18 | 22.2 | 13.4 | 15.6
19 | 21.2 | 12.7 | 13.8
20 | 18.7 | 11.9 | 12
21 | 16.8 | 11.1 | 9.9
22 | 14.8 | 10.5 | 8.6
23 | 14.4 | 10.1 | 8.8
0 | 14.1 | 10.7 | 9
1 | 12 | 10.1 | 8.4
2 | 10.6 | 9.8 | 7.9
3 | 10.2 | 9.5 | 7.9
4 | 9.9 | 9.3 | 7.8
5 | 10.5 | 9.5 | 8.1
6 | 11.1 | 10.5 | 8.4
7 | 14.2 | 11.8 | 9.5
8 | 16.2 | 13 | 11.4
9 | 19.6 | 14.1 | 12
10 | 21.5 | 15.1 | 13.6
11 | 22.8 | 15.9 | 15.3
12 | 24.8 | 16.6 | 15.4
13 | 25.6 | 17.1 | 16.1
14 | 26.1 | 17.4 | 15.9
15 | 25.5 | 17.6 | 16.4
16 | 25.2 | 17.2 | 16.1
17 | 24.4 | 16.8 | 15.1
18 | 23.5 | 16.1 | 15.4
19 | 21 | 15.2 | 14
20 | 18.2 | 14 | 12.8
21 | 16.6 | 12.8 | 11
22 | 14.5 | 11.9 | 10.6
23 | 13.9 | 11.3 | 10.5
0 | 13.4 | 8 | 10.5
1 | 11.4 | 7.4 | 9.6
2 | 9.8 | 7 | 9.1
3 | 9.6 | 6.7 | 8.9
4 | 9.6 | 6.5 | 8.8
5 | 9.5 | 6.7 | 9.1
6 | 10.8 | 7.8 | 9.3
7 | 12.2 | 9.3 | 10.9
8 | 15.1 | 10.6 | 12.4
9 | 17.2 | 11.8 | 14
10 | 18.9 | 12.9 | 15
11 | 19.5 | 13.9 | 15.7
12 | 20.5 | 14.6 | 16.6
13 | 21.6 | 15.2 | 16.5
14 | 21.4 | 15.5 | 17.7
15 | 21.6 | 15.7 | 17.1
16 | 22 | 15.3 | 17.7
17 | 20.3 | 14.8 | 17.3
18 | 20.3 | 14.1 | 17.1
19 | 18 | 13 | 14.7
20 | 16 | 11.7 | 14.1
21 | 14 | 10.4 | 12.7
22 | 13.5 | 9.4 | 11.4
23 | 12.7 | 8.7 | 12
0 | 12 | 12 | 12.6
1 | 11 | 11.5 | 13
2 | 10.1 | 11.3 | 13.2
3 | 9.8 | 11 | 13.1
4 | 9.6 | 10.9 | 12.9
5 | 9.9 | 11 | 12.6
6 | 10.3 | 11.8 | 13.6
7 | 12.8 | 13 | 14.5
8 | 14.9 | 14 | 15.5
9 | 17.1 | 14.8 | 16.9
10 | 19.2 | 15.7 | 17.9
11 | 20.8 | 16.4 | 19.3
12 | 21.2 | 17 | 20
13 | 22.1 | 17.4 | 19.9
14 | 21.5 | 17.6 | 19.7
15 | 22.5 | 17.8 | 20.3
16 | 21.6 | 17.5 | 20
17 | 20.9 | 17.1 | 20.3
18 | 20.4 | 16.6 | 19.1
19 | 18.6 | 15.8 | 17.7
20 | 16.9 | 14.8 | 16.8
21 | 15.2 | 13.8 | 15.4
22 | 13.3 | 13.1 | 14.5
23 | 13.3 | 12.5 | 14.3
0 | 13.2 | 11.3 | 14
1 | 12.8 | 10.8 | 12.6
2 | 12.5 | 10.6 | 12
3 | 12.4 | 10.3 | 11.5
4 | 12.3 | 10.2 | 11.6
5 | 12.4 | 10.3 | 11.8
6 | 12.6 | 11.1 | 11.8
7 | 13.6 | 12.2 | 13.8
8 | 14.6 | 13.3 | 14.9
9 | 15.2 | 14.1 | 16.7
10 | 15.8 | 15 | 18
11 | 17.4 | 15.7 | 19.3
12 | 17.8 | 16.3 | 20.4
13 | 17.4 | 16.7 | 20.7
14 | 17.5 | 16.9 | 20.7
15 | 17.6 | 17.1 | 19.8
16 | 17.9 | 16.8 | 20.1
17 | 17.5 | 16.4 | 20
18 | 17.5 | 15.9 | 19.1
19 | 16 | 15.1 | 18
20 | 14.8 | 14 | 16.8
21 | 14 | 13.1 | 15.3
22 | 14.1 | 12.3 | 14.5
23 | 13.8 | 11.8 | 13.4
0 | 13.6 | 11.9 | 12.3
1 | 12.2 | 11.5 | 9.8
2 | 11.2 | 11.2 | 8
3 | 11 | 11 | 7.8
4 | 10.8 | 10.9 | 7.8
5 | 10.9 | 11 | 7.8
6 | 11.1 | 11.8 | 9.4
7 | 12.6 | 12.8 | 11.1
8 | 14.3 | 13.8 | 14.1
9 | 15.9 | 14.6 | 15.8
10 | 16.2 | 15.3 | 17.8
11 | 16.9 | 16 | 19.8
12 | 18.5 | 16.6 | 20.5
13 | 17.5 | 16.9 | 21.5
14 | 18.8 | 17.2 | 21.9
15 | 18.8 | 17.3 | 22.5
16 | 17.9 | 17 | 21.8
17 | 18.2 | 16.7 | 21.3
18 | 18.4 | 16.2 | 19.9
19 | 16 | 15.4 | 18.8
20 | 15.1 | 14.5 | 16
21 | 13.9 | 13.6 | 13.9
22 | 12.9 | 12.9 | 12.6
23 | 12.6 | 12.4 | 11.9
0 | 12.3 | 8.5 | 11.2
1 | 11.2 | 7.6 | 10.3
2 | 10.3 | 7.1 | 9.7
3 | 10.3 | 6.5 | 9.3
4 | 10.3 | 6.3 | 9.2
5 | 10.6 | 6.6 | 9.1
6 | 10.9 | 8.2 | 10.5
7 | 12.8 | 10.4 | 12
8 | 14.8 | 12.4 | 14.6
9 | 16.7 | 14.1 | 16.8
10 | 17.4 | 15.8 | 18
11 | 19.1 | 17.3 | 18.9
12 | 19.5 | 18.4 | 20.4
13 | 19.7 | 19.2 | 21.3
14 | 19.7 | 19.7 | 21.6
15 | 20.3 | 20 | 21.8
16 | 19.8 | 19.4 | 21.9
17 | 19.6 | 18.6 | 20.7
18 | 17.7 | 17.6 | 19.7
19 | 17.1 | 16 | 18.4
20 | 15.7 | 14 | 16.7
21 | 14.5 | 12.1 | 14.7
22 | 12.9 | 10.6 | 12.5
23 | 12.9 | 9.6 | 12.7
0 | 12.9 | 8.3 | 12.8
1 | 11.7 | 7.1 | 12.1
2 | 11.2 | 6.4 | 11.7
3 | 10.7 | 5.8 | 11.3
4 | 10.9 | 5.4 | 11
5 | 11.1 | 5.8 | 11.2
6 | 11.2 | 7.8 | 11.5
7 | 12.6 | 10.6 | 13.4
8 | 14.2 | 13.1 | 15.3
9 | 15.3 | 15.3 | 17.1
10 | 15.9 | 17.3 | 17.9
11 | 17.3 | 19.1 | 19.2
12 | 17.5 | 20.5 | 20.7
13 | 18.4 | 21.5 | 20.4
14 | 17.9 | 22.2 | 20.7
15 | 17.9 | 22.5 | 21.3
16 | 18.5 | 21.7 | 21
17 | 18.1 | 20.8 | 21
18 | 16.9 | 19.5 | 20
19 | 16.2 | 17.6 | 17.8
20 | 14.7 | 15 | 16.8
21 | 13.7 | 12.7 | 15
22 | 13.1 | 10.8 | 14.2
23 | 13.1 | 9.6 | 14.5
0 | 13.1 | 9 | 14.8
1 | 12.8 | 8.1 | 14.9
2 | 12.5 | 7.6 | 14.8
3 | 12.4 | 7.1 | 14.7
4 | 12.3 | 6.8 | 14.8
5 | 12.5 | 7.1 | 14.9
6 | 12.7 | 8.7 | 14.8
7 | 13.4 | 10.9 | 15.3
8 | 14.6 | 12.9 | 16.4
9 | 15 | 14.6 | 17.5
10 | 16.4 | 16.3 | 17.3
11 | 17.2 | 17.7 | 18.1
12 | 17.2 | 18.8 | 18.2
13 | 17.2 | 19.6 | 18.8
14 | 17.1 | 20.2 | 18.2
15 | 17.7 | 20.5 | 18.5
16 | 17.2 | 19.8 | 18.2
17 | 17.3 | 19.1 | 18.6
18 | 16.9 | 18 | 18
19 | 15.8 | 16.5 | 17.5
20 | 14.9 | 14.5 | 17.1
21 | 14.2 | 12.6 | 16.5
22 | 13.8 | 11.1 | 15.8
23 | 13.1 | 10.1 | 15.7
0 | 12.5 | 11.7 | 15.6
1 | 10 | 10.8 | 13.9
2 | 8.5 | 10.3 | 12.8
3 | 8.5 | 9.8 | 12.8
4 | 8.5 | 9.6 | 12.8
5 | 8.5 | 9.9 | 12.8
6 | 9.2 | 11.4 | 12.8
7 | 10.1 | 13.5 | 13.6
8 | 12.5 | 15.4 | 14.4
9 | 13.8 | 17 | 15.2
10 | 14.9 | 18.5 | 16
11 | 16.1 | 19.9 | 16.4
12 | 17.2 | 20.9 | 16.5
13 | 17.4 | 21.7 | 16.5
14 | 17.3 | 22.2 | 16.7
15 | 17.8 | 22.5 | 16.7
16 | 17.1 | 21.9 | 17.1
17 | 17.3 | 21.2 | 17.1
18 | 16.6 | 20.2 | 16.3
19 | 14.9 | 18.7 | 15.5
20 | 13.8 | 16.8 | 14.8
21 | 12 | 15 | 14.1
22 | 10.5 | 13.6 | 14.3
23 | 11.6 | 12.7 | 13.5
0 | 12.7 | 13.5 | 12.7
1 | 12.9 | 12.9 | 10.2
2 | 13.1 | 12.6 | 8.7
3 | 12.9 | 12.2 | 8.5
4 | 12.7 | 12.1 | 8.5
5 | 12.8 | 12.3 | 8.5
6 | 12.9 | 13.3 | 8.8
7 | 13.2 | 14.7 | 9.3
8 | 14 | 16 | 10.4
9 | 15.5 | 17.2 | 11
10 | 15.6 | 18.2 | 10.8
11 | 16.3 | 19.2 | 11.3
12 | 16.2 | 19.9 | 11.7
13 | 16.3 | 20.4 | 12.1
14 | 16.4 | 20.8 | 12.5
15 | 16.7 | 21 | 12
16 | 16.6 | 20.5 | 11.7
17 | 16.4 | 20.1 | 12.4
18 | 16.1 | 19.4 | 11.9
19 | 15.7 | 18.4 | 11.1
20 | 14.4 | 17.1 | 10.3
21 | 14.3 | 15.8 | 9.9
22 | 13.8 | 14.9 | 9.2
23 | 13 | 14.2 | 9.4
0 | 12.1 | 14.8 | 9.5
1 | 9.8 | 14.4 | 9
2 | 8 | 14.1 | 8.7
3 | 8 | 13.9 | 8.5
4 | 8 | 13.8 | 8.4
5 | 8.6 | 13.9 | 8.6
6 | 9.3 | 14.6 | 8.8
7 | 11.6 | 15.6 | 10.2
8 | 14.1 | 16.4 | 12.2
9 | 16.3 | 17.2 | 13.7
10 | 18.1 | 17.9 | 14.3
11 | 19.2 | 18.5 | 15.5
12 | 21.1 | 19 | 16.8
13 | 21.7 | 19.3 | 16.8
14 | 22.3 | 19.5 | 17
15 | 21.5 | 19.7 | 17.3
16 | 21.3 | 19.4 | 16.9
17 | 21.5 | 19.1 | 16.3
18 | 19.8 | 18.6 | 16.3
19 | 17.1 | 17.9 | 14.2
20 | 15.7 | 17.1 | 13.7
21 | 13.7 | 16.3 | 12.4
22 | 12.2 | 15.6 | 11
23 | 11.9 | 15.2 | 10.9
0 | 11.5 | 15.2 | 10.8
1 | 10.4 | 15 | 9.4
2 | 9.9 | 14.9 | 8.9
3 | 9.4 | 14.7 | 8.5
4 | 9 | 14.7 | 8.5
5 | 9.4 | 14.7 | 8.7
6 | 9.8 | 15.1 | 8.5
7 | 11.8 | 15.7 | 9.1
8 | 14.2 | 16.2 | 10.7
9 | 15.9 | 16.6 | 11.7
10 | 17 | 17 | 12.2
11 | 18.8 | 17.4 | 12.5
12 | 19.5 | 17.6 | 13.4
13 | 20.7 | 17.8 | 13.1
14 | 20.4 | 18 | 13.1
15 | 20.9 | 18 | 13.7
16 | 20.8 | 17.9 | 13.4
17 | 20.2 | 17.7 | 13.3
18 | 19 | 17.4 | 12.7
19 | 16.7 | 17.1 | 12.4
20 | 15.2 | 16.6 | 11.8
21 | 13.6 | 16.1 | 10.2
22 | 12.5 | 15.7 | 9.6
23 | 11.6 | 15.5 | 9.3
0 | 10.7 | 13 | 9.1
1 | 7.9 | 12.4 | 7.5
2 | 5.7 | 12.1 | 6.5
3 | 5.6 | 11.7 | 6.1
4 | 5.6 | 11.6 | 5.8
5 | 6.1 | 11.8 | 6.3
6 | 6.6 | 12.8 | 6.8
7 | 9.4 | 14.1 | 8.6
8 | 12.3 | 15.4 | 12
9 | 14.5 | 16.5 | 14
10 | 16.8 | 17.5 | 15.5
11 | 17.9 | 18.4 | 16.6
12 | 19.1 | 19.1 | 19.1
13 | 20.5 | 19.6 | 19.7
14 | 20.7 | 19.9 | 19.5
15 | 21.2 | 20.1 | 20.1
16 | 20.7 | 19.7 | 20.1
17 | 19.9 | 19.3 | 19
18 | 18.7 | 18.6 | 18.1
19 | 16 | 17.6 | 16.2
20 | 13.9 | 16.4 | 13.5
21 | 11.5 | 15.2 | 11.5
22 | 10.8 | 14.3 | 9.8
23 | 10.8 | 13.6 | 9.4
0 | 10.8 | 12.1 | 9
1 | 10.8 | 11.5 | 6.9
2 | 10.8 | 11.1 | 5.5
3 | 10.7 | 10.8 | 4.9
4 | 10.6 | 10.6 | 4.9
5 | 10.8 | 10.8 | 4.9
6 | 11 | 11.9 | 6.5
7 | 11.7 | 13.3 | 8.2
8 | 12.2 | 14.6 | 11.5
9 | 13.1 | 15.8 | 13.7
10 | 13.7 | 16.8 | 15.6
11 | 14.6 | 17.8 | 17.5
12 | 14.1 | 18.5 | 19.6
13 | 14.2 | 19.1 | 19.5
14 | 15.1 | 19.4 | 20.7
15 | 14.6 | 19.6 | 19.6
16 | 14.8 | 19.2 | 19.8
17 | 14.6 | 18.7 | 19.5
18 | 14.8 | 18 | 18.7
19 | 13.4 | 17 | 17.1
20 | 13.4 | 15.7 | 13.9
21 | 12.3 | 14.4 | 10.5
22 | 11.9 | 13.4 | 9.3
23 | 12 | 12.8 | 9.4
0 | 12.2 | 12.9 | 9.5
1 | 11.1 | 12.5 | 8.3
2 | 10.7 | 12.2 | 7.4
3 | 10.3 | 11.9 | 7.5
4 | 10.4 | 11.8 | 7.3
5 | 10.6 | 12 | 7.5
6 | 10.4 | 12.8 | 7.8
7 | 11.5 | 13.9 | 10.4
8 | 13.1 | 14.9 | 11.4
9 | 14.4 | 15.8 | 13.3
10 | 15.1 | 16.6 | 15.6
11 | 15.8 | 17.3 | 16.5
12 | 16.2 | 17.9 | 17.7
13 | 16.2 | 18.3 | 17.9
14 | 16.7 | 18.6 | 18.5
15 | 16.2 | 18.7 | 18.2
16 | 16.4 | 18.4 | 18.3
17 | 15.9 | 18 | 17.5
18 | 15.5 | 17.5 | 17.2
19 | 15 | 16.7 | 15.8
20 | 13.9 | 15.7 | 13.4
21 | 13.1 | 14.7 | 11.6
22 | 11.8 | 14 | 10.8
23 | 12.2 | 12.7 | 11.7
0 | 12.6 | 11.4 | 12.6
1 | 13.1 | 10.1 | 13.6
2 | 13.5 | 8.8 | 14.5
3 | 13.1 | 8.1 | 14.4
4 | 13.1 | 8.1 | 14.4
5 | 13 | 8.7 | 15.1
6 | 14.5 | 10.5 | 15.8
7 | 15.9 | 12.8 | 18.7
8 | 18 | 15 | 20.5
9 | 19.3 | 16.9 | 23.4
10 | 20.4 | 18.7 | 25.3
11 | 21.9 | 20.2 | 27
12 | 22 | 21.4 | 27.7
13 | 23.5 | 22.3 | 29
14 | 24 | 22.8 | 29.2
15 | 23.6 | 23.3 | 29.8
16 | 23.8 | 22.6 | 29.2
17 | 23.1 | 21.8 | 29.1
18 | 22.2 | 20.7 | 27
19 | 21 | 19.1 | 25.5
20 | 18.9 | 16.9 | 23
21 | 18.3 | 14.7 | 21.4
22 | 16.2 | 12.7 | 18.8
23 | 16.2 | 11.6 | 17.5
0 | 16.1 | 9.5 | 16.1
1 | 15.2 | 8.8 | 12.7
2 | 14.3 | 8.3 | 10.2
3 | 14.3 | 7.8 | 10.2
4 | 14.2 | 7.8 | 10.2
5 | 14.9 | 8.2 | 10.2
6 | 15.5 | 9.4 | 12.3
7 | 16.8 | 10.9 | 14.6
8 | 18.8 | 12.3 | 16.6
9 | 20.1 | 13.6 | 19.8
10 | 21.7 | 14.8 | 21.7
11 | 22.7 | 15.8 | 23.3
12 | 23.1 | 16.5 | 24.3
13 | 24.1 | 17.1 | 26.4
14 | 23.9 | 17.5 | 26.4
15 | 24.4 | 17.8 | 26.2
16 | 23.9 | 17.3 | 27.1
17 | 23.9 | 16.8 | 24.7
18 | 23.2 | 16.1 | 24
19 | 21.9 | 15 | 22.6
20 | 19.1 | 13.6 | 19.5
21 | 17.7 | 12.1 | 17.4
22 | 16.6 | 10.9 | 15.5
23 | 15.7 | 10.2 | 14.5
0 | 14.8 | 9.4 | 13.5
1 | 11.8 | 8.7 | 10.9
2 | 9.7 | 8.2 | 9.3
3 | 9.6 | 7.8 | 8.8
4 | 9.6 | 7.8 | 8.8
5 | 9.9 | 8.2 | 8.8
6 | 10.3 | 9.4 | 10.4
7 | 12.4 | 10.9 | 12.2
8 | 14.5 | 12.3 | 13.9
9 | 15.2 | 13.6 | 15.5
10 | 16.7 | 14.8 | 17.6
11 | 18 | 15.8 | 20.6
12 | 18.9 | 16.6 | 20.1
13 | 19.5 | 17.2 | 21.8
14 | 20.1 | 17.5 | 22.4
15 | 19.4 | 17.9 | 21.8
16 | 18.9 | 17.4 | 21.7
17 | 19.2 | 16.9 | 21.1
18 | 17.9 | 16.1 | 21.1
19 | 16.9 | 15 | 18.4
20 | 15.3 | 13.6 | 16.1
21 | 14 | 12.1 | 14.3
22 | 12.2 | 10.9 | 12.2
23 | 12.7 | 10.1 | 12.2
0 | 13.2 | 8.7 | 12.2
1 | 12.9 | 8.1 | 10.9
2 | 12.5 | 7.7 | 10.1
3 | 12.5 | 7.3 | 10
4 | 12.5 | 7.3 | 9.9
5 | 13.1 | 7.6 | 10.3
6 | 13.6 | 8.7 | 10.7
7 | 15.2 | 9.9 | 11
8 | 15.3 | 11.1 | 12.6
9 | 17.1 | 12.2 | 13.6
10 | 18.6 | 13.2 | 15.1
11 | 19.4 | 14.1 | 14.9
12 | 19.9 | 14.7 | 16
13 | 20.2 | 15.2 | 15.7
14 | 20.8 | 15.5 | 16
15 | 19.8 | 15.8 | 16.6
16 | 19.6 | 15.4 | 16.1
17 | 20.8 | 15 | 16.2
18 | 19.2 | 14.3 | 15.8
19 | 18.3 | 13.4 | 13.9
20 | 16.8 | 12.2 | 14.1
21 | 16.6 | 11 | 13
22 | 14.8 | 9.9 | 11.4
23 | 15 | 9.3 | 11.8
0 | 15.3 | 10.3 | 12.2
1 | 14.7 | 9.8 | 11.2
2 | 14.6 | 9.5 | 10.8
3 | 14.1 | 9.2 | 10.4
4 | 13.6 | 9.2 | 10.5
5 | 13.9 | 9.4 | 10.5
6 | 14.2 | 10.2 | 11.5
7 | 16.2 | 11.2 | 12.8
8 | 18.5 | 12.2 | 15.6
9 | 19.7 | 13 | 16.3
10 | 20.6 | 13.8 | 18.9
11 | 22.7 | 14.5 | 19.8
12 | 22 | 15 | 21.2
13 | 23.9 | 15.4 | 21.2
14 | 24.1 | 15.6 | 22.3
15 | 23.5 | 15.9 | 22
16 | 23.8 | 15.5 | 21.7
17 | 22.9 | 15.2 | 21.1
18 | 22.4 | 14.7 | 21.1
19 | 21.6 | 14 | 19.1
20 | 19.4 | 13 | 16.7
21 | 17.7 | 12.1 | 15.7
22 | 16.2 | 11.2 | 14.7
23 | 16.5 | 10.7 | 13.9
0 | 16.8 | 7.6 | 13
1 | 16 | 6.8 | 11.1
2 | 15.5 | 6.2 | 9.5
3 | 15.3 | 5.7 | 9.5
4 | 15.3 | 5.7 | 9.4
5 | 15.3 | 6.2 | 9.9
6 | 15.9 | 7.5 | 10.6
7 | 16.5 | 9.3 | 12.2
8 | 16.6 | 10.9 | 14.8
9 | 17.2 | 12.3 | 17
10 | 18.4 | 13.7 | 17.7
11 | 19 | 14.8 | 19.8
12 | 19.5 | 15.7 | 20.4
13 | 19.2 | 16.3 | 22.1
14 | 19.2 | 16.8 | 21.8
15 | 19.2 | 17.1 | 22
16 | 19 | 16.6 | 22.5
17 | 19 | 16 | 22.2
18 | 19.2 | 15.2 | 20.9
19 | 18.2 | 13.9 | 18.8
20 | 17.5 | 12.3 | 17.5
21 | 16.6 | 10.6 | 15.1
22 | 16.6 | 9.2 | 13.1
23 | 15.6 | 8.4 | 12.2
0 | 14.6 | 7.3 | 11.2
1 | 11.6 | 6 | 9
2 | 9.3 | 5.1 | 7.9
3 | 9.3 | 4.3 | 7
4 | 9.3 | 4.3 | 7.1
5 | 9.7 | 5 | 7.2
6 | 10.3 | 7.2 | 8.6
7 | 12.5 | 9.8 | 10.4
8 | 14.2 | 12.3 | 12.6
9 | 16.8 | 14.6 | 14.9
10 | 18.1 | 16.7 | 17.2
11 | 19.6 | 18.5 | 18.9
12 | 20.3 | 19.9 | 19.9
13 | 21.6 | 20.9 | 19.6
14 | 21.4 | 21.5 | 20.9
15 | 21.4 | 22.1 | 21.3
16 | 22.1 | 21.3 | 20.5
17 | 20.6 | 20.3 | 20.8
18 | 19.5 | 19 | 18.3
19 | 17.9 | 17.1 | 17.3
20 | 16.2 | 14.6 | 15
21 | 14.7 | 12 | 12.7
22 | 12.2 | 9.8 | 10.6
23 | 12.8 | 8.5 | 10.3
0 | 13.3 | 8 | 9.9
1 | 12.4 | 7.4 | 7.8
2 | 11.9 | 7 | 6.5
3 | 12.2 | 6.6 | 6.1
4 | 12.3 | 6.6 | 5.8
5 | 12 | 6.9 | 6.3
6 | 12.1 | 8 | 6.8
7 | 12.1 | 9.3 | 8.7
8 | 13 | 10.6 | 10.8
9 | 12.9 | 11.8 | 12.8
10 | 14.4 | 12.8 | 14.8
11 | 14 | 13.7 | 15.5
12 | 14.5 | 14.4 | 16.4
13 | 13.9 | 14.9 | 16.9
14 | 14 | 15.3 | 18.3
15 | 14.6 | 15.6 | 18
16 | 14.4 | 15.1 | 17.6
17 | 14.4 | 14.7 | 17.5
18 | 14.2 | 14 | 15.6
19 | 14.1 | 13.1 | 14.9
20 | 13.2 | 11.8 | 12.3
21 | 12.4 | 10.4 | 11.3
22 | 12.1 | 9.3 | 10
23 | 12.7 | 8.7 | 10
0 | 13.2 | 9.5 | 10
1 | 12.6 | 8.8 | 9.7
2 | 12.2 | 8.3 | 9.2
3 | 12 | 7.9 | 9.1
4 | 12 | 7.9 | 9.1
5 | 11.9 | 8.3 | 9
6 | 12.1 | 9.5 | 10
7 | 12.4 | 11 | 11
8 | 13.2 | 12.4 | 12
9 | 13.5 | 13.7 | 13.2
10 | 13.9 | 14.9 | 14.5
11 | 14.2 | 16 | 14.6
12 | 14.4 | 16.7 | 15.3
13 | 14.4 | 17.3 | 16.5
14 | 14.3 | 17.7 | 16.1
15 | 14.7 | 18 | 16.6
16 | 14.9 | 17.5 | 16
17 | 14.6 | 17 | 16.1
18 | 14.4 | 16.3 | 15
19 | 14.1 | 15.2 | 15.1
20 | 13.2 | 13.7 | 12.8
21 | 13.2 | 12.2 | 12
22 | 12.1 | 11 | 11.1
23 | 13.3 | 10.2 | 11.3
0 | 14.5 | 11.8 | 11.5
1 | 14.7 | 11.1 | 10.7
2 | 14.9 | 10.7 | 10.2
3 | 14.6 | 10.3 | 10.1
4 | 14.7 | 10.3 | 10.1
5 | 14.5 | 10.6 | 10.3
6 | 15.5 | 11.7 | 10.5
7 | 16.5 | 13.1 | 11.2
8 | 17.4 | 14.5 | 12.5
9 | 18.2 | 15.7 | 13.7
10 | 19.9 | 16.8 | 13.8
11 | 20.3 | 17.7 | 14.2
12 | 21.7 | 18.4 | 14.8
13 | 21.2 | 18.9 | 15.6
14 | 20.9 | 19.3 | 14.9
15 | 21.3 | 19.6 | 15.6
16 | 21.1 | 19.1 | 15.3
17 | 21.2 | 18.7 | 15.2
18 | 20.1 | 18 | 14.7
19 | 19.6 | 17 | 13.8
20 | 18.7 | 15.7 | 13.6
21 | 16.9 | 14.3 | 12.4
22 | 16.6 | 13.1 | 11.3
23 | 16.9 | 12.4 | 11.2
0 | 17.3 | 15.6 | 11.2
1 | 17 | 15.1 | 9.7
2 | 16.9 | 14.7 | 9
3 | 16.7 | 14.4 | 8.4
4 | 16.4 | 14.4 | 8.4
5 | 16.6 | 14.7 | 8.4
6 | 16.8 | 15.5 | 9.2
7 | 17.6 | 16.6 | 10.7
8 | 18.7 | 17.5 | 12.2
9 | 19.1 | 18.4 | 13.9
10 | 20.1 | 19.2 | 14.7
11 | 20.5 | 19.9 | 15.3
12 | 20.8 | 20.4 | 16.8
13 | 21 | 20.8 | 17.5
14 | 20.9 | 21.1 | 18
15 | 21.3 | 21.3 | 17.3
16 | 20.3 | 21 | 18
17 | 20.7 | 20.6 | 17.2
18 | 20.6 | 20.1 | 16.7
19 | 19.9 | 19.4 | 15.3
20 | 18.9 | 18.4 | 14.2
21 | 18.3 | 17.4 | 12.3
22 | 17.6 | 16.5 | 11.3
23 | 17.7 | 16 | 11.7
0 | 17.9 | 17.5 | 12.1
1 | 16.6 | 16.9 | 11.8
2 | 15.9 | 16.5 | 11.5
3 | 15.6 | 16.2 | 11.2
4 | 15.4 | 16.2 | 11.2
5 | 15.4 | 16.5 | 11.2
6 | 15.5 | 17.5 | 11.6
7 | 15.6 | 18.7 | 14
8 | 17.3 | 19.8 | 15.2
9 | 17.7 | 20.8 | 17.3
10 | 19 | 21.7 | 19.4
11 | 19.3 | 22.6 | 19.6
12 | 18.9 | 23.2 | 20.4
13 | 19.2 | 23.6 | 21.1
14 | 19.3 | 23.9 | 22
15 | 19.1 | 24.2 | 21.6
16 | 19.7 | 23.8 | 21.9
17 | 19 | 23.4 | 21.9
18 | 18.6 | 22.8 | 20.7
19 | 18.4 | 21.9 | 19
20 | 17.4 | 20.8 | 18.1
21 | 17.5 | 19.6 | 15.3
22 | 16.2 | 18.6 | 13.7
23 | 15.9 | 18 | 14.2
0 | 15.6 | 16.8 | 14.6
1 | 13.6 | 16.4 | 14.2
2 | 11.9 | 16 | 13.8
3 | 11.8 | 15.8 | 13.6
4 | 11.8 | 15.8 | 13.5
5 | 12.3 | 16 | 13.4
6 | 12.9 | 16.8 | 14.3
7 | 14.5 | 17.8 | 15.3
8 | 17.2 | 18.7 | 16.5
9 | 18.2 | 19.6 | 17.9
10 | 19.4 | 20.4 | 19.3
11 | 21.6 | 21 | 19.7
12 | 22.5 | 21.5 | 20.4
13 | 23.7 | 21.9 | 21.1
14 | 23 | 22.2 | 21.6
15 | 23.2 | 22.4 | 21.6
16 | 23.7 | 22.1 | 21
17 | 22.5 | 21.7 | 20.4
18 | 21.9 | 21.2 | 20.9
19 | 19.9 | 20.5 | 19.2
20 | 18.4 | 19.6 | 17.7
21 | 16.7 | 18.6 | 17.1
22 | 15.1 | 17.8 | 15.5
23 | 15.3 | 17.3 | 15.7
0 | 15.6 | 18.8 | 15.9
1 | 15 | 18.2 | 14.7
2 | 14.4 | 17.9 | 13.7
3 | 14.3 | 17.5 | 13.6
4 | 14.2 | 17.5 | 13.5
5 | 14.8 | 17.8 | 14
6 | 15.3 | 18.7 | 14.6
7 | 17.8 | 19.9 | 15.7
8 | 19.9 | 20.9 | 17.5
9 | 21.6 | 21.9 | 18.8
10 | 23.5 | 22.8 | 20.1
11 | 23.8 | 23.6 | 20.5
12 | 26.3 | 24.1 | 22
13 | 25.8 | 24.6 | 22.4
14 | 26.7 | 24.8 | 22.2
15 | 27.3 | 25.1 | 22.8
16 | 26.5 | 24.7 | 22.5
17 | 26.3 | 24.3 | 21.8
18 | 25.5 | 23.8 | 21
19 | 23.6 | 23 | 20.4
20 | 22.1 | 21.9 | 18.3
21 | 19 | 20.8 | 17.7
22 | 18.3 | 19.8 | 15.6
23 | 17.5 | 19.3 | 15.6
0 | 16.6 | 15.7 | 15.7
1 | 14 | 15.2 | 14.3
2 | 12.1 | 14.9 | 13.2
3 | 12.3 | 14.5 | 13
4 | 12.1 | 14.5 | 12.9
5 | 12 | 14.8 | 13.5
6 | 14.7 | 15.7 | 14.2
7 | 17.5 | 16.8 | 15.4
8 | 19.3 | 17.8 | 17.6
9 | 22.8 | 18.7 | 19
10 | 25 | 19.6 | 20.8
11 | 26.8 | 20.3 | 22.2
12 | 28.6 | 20.9 | 22.9
13 | 29.3 | 21.3 | 23.2
14 | 30 | 21.6 | 24.2
15 | 30.6 | 21.8 | 24.3
16 | 29.4 | 21.4 | 23.5
17 | 28.2 | 21.1 | 24
18 | 27.2 | 20.5 | 22.2
19 | 25.4 | 19.8 | 21.2
20 | 22.9 | 18.7 | 19.7
21 | 20 | 17.7 | 17.7
22 | 17.5 | 16.8 | 15.9
23 | 17.2 | 16.2 | 15.6
0 | 16.9 | 14.7 | 15.3
1 | 15.8 | 13.9 | 13.8
2 | 15.1 | 13.3 | 13.1
3 | 15.2 | 12.9 | 12.5
4 | 15.1 | 12.8 | 12.6
5 | 15 | 13.3 | 12.7
6 | 16.4 | 14.7 | 12.6
7 | 17.7 | 16.4 | 14.6
8 | 19.8 | 18 | 15.7
9 | 21.4 | 19.4 | 18.2
10 | 23.1 | 20.7 | 19.3
11 | 24.8 | 21.9 | 21.2
12 | 25.4 | 22.8 | 21.5
13 | 25.8 | 23.5 | 22.4
14 | 26.9 | 24 | 22.8
15 | 26.3 | 24.4 | 22.4
16 | 26.4 | 23.9 | 22.3
17 | 25.4 | 23.3 | 22.2
18 | 26 | 22.5 | 21.1
19 | 23 | 21.2 | 20.7
20 | 21.6 | 19.6 | 17.8
21 | 19.4 | 17.9 | 17
22 | 18.9 | 16.5 | 15.7
23 | 21.4 | 15.5 | 15
0 | 23.8 | 16 | 14.4
1 | 23.9 | 15.1 | 11.8
2 | 23.9 | 14.5 | 10.1
3 | 24.1 | 13.9 | 10.2
4 | 24 | 13.9 | 10.1
5 | 23.8 | 14.4 | 10.1
6 | 23.9 | 16 | 11.1
7 | 24 | 18 | 12.2
8 | 25.1 | 19.8 | 13.2
9 | 25.4 | 21.5 | 15.2
10 | 26 | 23 | 16.2
11 | 27.2 | 24.3 | 17.6
12 | 26.7 | 25.4 | 18.2
13 | 26.6 | 26.2 | 18.6
14 | 27.2 | 26.8 | 19
15 | 27.2 | 27.2 | 18.6
16 | 27.2 | 26.6 | 19.5
17 | 27.2 | 26 | 18.9
18 | 26.6 | 25 | 17.7
19 | 25.9 | 23.6 | 17
20 | 25.3 | 21.7 | 15
21 | 24.8 | 19.7 | 13.9
22 | 25.1 | 18.1 | 13.1
23 | 24.1 | 17 | 12.5
0 | 23.1 | 14.8 | 12
1 | 19.6 | 14.1 | 9.1
2 | 17.5 | 13.7 | 8.1
3 | 17.3 | 13.3 | 7.2
4 | 17.3 | 13.3 | 7.2
5 | 17.3 | 13.7 | 7.4
6 | 17.7 | 14.7 | 7.4
7 | 18.4 | 16 | 8.9
8 | 18.9 | 17.3 | 10.7
9 | 19.9 | 18.3 | 11.9
10 | 21.8 | 19.3 | 13.2
11 | 22.3 | 20.2 | 14.4
12 | 22.7 | 20.9 | 15.2
13 | 22.9 | 21.5 | 15.3
14 | 22.9 | 21.9 | 16
15 | 23 | 22.1 | 16.5
16 | 23.7 | 21.7 | 15.8
17 | 22.9 | 21.3 | 15.8
18 | 23 | 20.7 | 14.9
19 | 21.8 | 19.7 | 13.9
20 | 20.3 | 18.5 | 12.5
21 | 19.3 | 17.2 | 10.7
22 | 18.8 | 16.1 | 9.3
23 | 18.2 | 15.4 | 9.4
0 | 17.6 | 14.7 | 9.4
1 | 14.7 | 14.1 | 7.6
2 | 12.8 | 13.6 | 6.4
3 | 12.8 | 13.3 | 6.3
4 | 12.8 | 13.2 | 6.3
5 | 12.8 | 13.6 | 6.4
6 | 13.6 | 14.7 | 6.6
7 | 14.5 | 16 | 8.7
8 | 15.8 | 17.2 | 9.5
9 | 17.2 | 18.3 | 11.3
10 | 18.4 | 19.4 | 12.4
11 | 18.8 | 20.2 | 12.6
12 | 19.2 | 21 | 13.6
13 | 19.8 | 21.5 | 13.9
14 | 20.1 | 21.9 | 14.9
15 | 20.7 | 22.2 | 14.9
16 | 20 | 21.8 | 14.5
17 | 19.7 | 21.3 | 14
18 | 19.3 | 20.7 | 13.3
19 | 19 | 19.7 | 12.5
20 | 16.4 | 18.5 | 11.1
21 | 15.4 | 17.2 | 10.4
22 | 15.2 | 16 | 8.9
23 | 14.8 | 15.3 | 10.1
0 | 14.4 | 14.7 | 11.3
1 | 12.3 | 14.2 | 11.5
2 | 10.6 | 13.8 | 11.7
3 | 10.3 | 13.4 | 11.3
4 | 10 | 13.4 | 11.3
5 | 10.6 | 13.8 | 11.3
6 | 11.2 | 14.7 | 12
7 | 13.8 | 15.9 | 12.8
8 | 17 | 17 | 13.1
9 | 19.5 | 18 | 14.9
10 | 21.3 | 18.9 | 15.9
11 | 22.8 | 19.7 | 16.3
12 | 25.1 | 20.4 | 16.9
13 | 26.4 | 20.9 | 17.3
14 | 26.2 | 21.2 | 17.6
15 | 26.7 | 21.5 | 17.3
16 | 26.3 | 21.1 | 17.9
17 | 25 | 20.7 | 16.9
18 | 23.4 | 20.1 | 17.2
19 | 21.7 | 19.3 | 16.3
20 | 19.2 | 18.1 | 15.3
21 | 16.7 | 17 | 14.2
22 | 15 | 16 | 13.3
23 | 14.8 | 15.3 | 13.8
0 | 14.6 | 10.3 | 14.3
1 | 13 | 9.6 | 13.9
2 | 11.6 | 9.2 | 13.6
3 | 11.6 | 8.8 | 13.4
4 | 11.5 | 8.8 | 13.6
5 | 12 | 9.2 | 13.8
6 | 12.5 | 10.3 | 13.8
7 | 14.8 | 11.7 | 14.8
8 | 17.2 | 12.9 | 16
9 | 18.7 | 14.1 | 17.8
10 | 21.1 | 15.1 | 18.9
11 | 22.1 | 16.1 | 19.8
12 | 23.8 | 16.8 | 20.7
13 | 23.7 | 17.4 | 20.9
14 | 23.9 | 17.8 | 21.3
15 | 24.9 | 18.1 | 21.2
16 | 23.7 | 17.7 | 21.6
17 | 24.9 | 17.2 | 20.9
18 | 22.7 | 16.5 | 20.3
19 | 21.7 | 15.5 | 19.6
20 | 18.9 | 14.2 | 18.5
21 | 17.2 | 12.9 | 17.2
22 | 15.1 | 11.7 | 16.5
23 | 15.4 | 11 | 15.5
0 | 15.6 | 9.9 | 14.5
1 | 14.2 | 9.1 | 11.7
2 | 13.2 | 8.5 | 9.8
3 | 13.2 | 8 | 9.7
4 | 13.2 | 7.9 | 9.7
5 | 13.1 | 8.4 | 9.8
6 | 14.5 | 9.9 | 10.1
7 | 16 | 11.6 | 12.6
8 | 17 | 13.3 | 15.1
9 | 19.4 | 14.8 | 16.3
10 | 20.6 | 16.1 | 18.3
11 | 21.2 | 17.3 | 18.9
12 | 22.1 | 18.3 | 20.3
13 | 23.2 | 19.1 | 21.3
14 | 23.8 | 19.6 | 21.8
15 | 23.8 | 19.9 | 21.9
16 | 23 | 19.4 | 22.3
17 | 23.3 | 18.8 | 21.2
18 | 22.7 | 17.9 | 19.9
19 | 21 | 16.6 | 19.6
20 | 19 | 15 | 16.9
21 | 17.5 | 13.2 | 15.5
22 | 16.2 | 11.7 | 13.4
23 | 15.2 | 10.8 | 13.4
0 | 14.2 | 13.2 | 13.3
1 | 11 | 12.5 | 12
2 | 8.9 | 12.1 | 11
3 | 8.9 | 11.6 | 11
4 | 8.9 | 11.6 | 11
5 | 9.1 | 12 | 10.9
6 | 9.4 | 13.2 | 11.7
7 | 11.2 | 14.6 | 12.5
8 | 13.6 | 15.9 | 14.1
9 | 15.2 | 17.1 | 15.8
10 | 16.9 | 18.2 | 17
11 | 18.4 | 19.2 | 18.3
12 | 18.7 | 20 | 18.6
13 | 19.1 | 20.6 | 19.5
14 | 19.3 | 21 | 20.1
15 | 20.3 | 21.3 | 19.4
16 | 20.4 | 20.9 | 19.7
17 | 19.6 | 20.4 | 19.8
18 | 18.8 | 19.7 | 19.3
19 | 17 | 18.6 | 18
20 | 15.7 | 17.3 | 16.6
21 | 12.7 | 15.9 | 15
22 | 12.2 | 14.7 | 14.1
23 | 12.6 | 13.9 | 13.6
0 | 13 | 11.9 | 13.1
1 | 12.2 | 11.1 | 11
2 | 11.6 | 10.5 | 9.5
3 | 11.5 | 10 | 9.4
4 | 11.4 | 10 | 9.4
5 | 11.8 | 10.5 | 9.6
6 | 12.3 | 11.9 | 9.9
7 | 14.3 | 13.6 | 12.4
8 | 16 | 15.3 | 15
9 | 18.2 | 16.7 | 16.8
10 | 19.8 | 18.1 | 18
11 | 21.7 | 19.3 | 20
12 | 22.6 | 20.2 | 20.9
13 | 22.6 | 21 | 21.7
14 | 23.1 | 21.5 | 22.8
15 | 23.7 | 21.9 | 22.5
16 | 23.4 | 21.3 | 22.5
17 | 22.9 | 20.7 | 21.4
18 | 22.1 | 19.9 | 21.1
19 | 20.2 | 18.6 | 20
20 | 18.2 | 16.9 | 17.4
21 | 16.4 | 15.2 | 15.3
22 | 14.9 | 13.7 | 13.5
23 | 15.6 | 12.8 | 13.3
0 | 16.2 | 13.6 | 13.1
1 | 16.4 | 13 | 11.6
2 | 16.5 | 12.7 | 10.4
3 | 16.4 | 12.3 | 10.3
4 | 16.2 | 12.3 | 10.2
5 | 16.3 | 12.6 | 10.6
6 | 16.3 | 13.6 | 10.9
7 | 17.8 | 14.7 | 13.1
8 | 19.8 | 15.8 | 16.2
9 | 20.5 | 16.8 | 18.1
10 | 21.7 | 17.7 | 19.5
11 | 22.5 | 18.5 | 21.1
12 | 22.7 | 19.2 | 22.1
13 | 23.5 | 19.7 | 23.3
14 | 23.5 | 20 | 23.5
15 | 23.3 | 20.2 | 24.3
16 | 23.8 | 19.9 | 24
17 | 23.6 | 19.5 | 23.5
18 | 22.9 | 18.9 | 22.5
19 | 21.5 | 18.1 | 20.7
20 | 20.2 | 16.9 | 18.3
21 | 18.9 | 15.8 | 16
22 | 18.6 | 14.8 | 14.6
23 | 18 | 14.2 | 14.3
0 | 17.4 | 11.1 | 14.1
1 | 15.5 | 10.1 | 12
2 | 14.3 | 9.4 | 10.6
3 | 14.3 | 8.9 | 10.6
4 | 14.2 | 8.8 | 10.4
5 | 14.3 | 9.4 | 10.9
6 | 14.4 | 11 | 11.4
7 | 14.7 | 13.1 | 13.6
8 | 15.3 | 15 | 16
9 | 16.1 | 16.7 | 17.7
10 | 16.2 | 18.3 | 19.9
11 | 17.5 | 19.6 | 22.3
12 | 17.6 | 20.7 | 22.2
13 | 18 | 21.6 | 23.9
14 | 17.4 | 22.2 | 24.7
15 | 17.4 | 22.6 | 24
16 | 16.9 | 22 | 24
17 | 17.4 | 21.3 | 23.6
18 | 17.4 | 20.3 | 23.4
19 | 17.9 | 18.8 | 21
20 | 16.4 | 16.9 | 19.2
21 | 15.3 | 14.9 | 16.4
22 | 14.6 | 13.1 | 15
23 | 15 | 12.1 | 14.4
0 | 15.3 | 14.5 | 13.8
1 | 13.5 | 13.9 | 11.6
2 | 12.7 | 13.6 | 10
3 | 12.1 | 13.3 | 9.8
4 | 12.2 | 13.3 | 9.7
5 | 12.4 | 13.6 | 9.6
6 | 12.4 | 14.4 | 10.9
7 | 14 | 15.5 | 12.3
8 | 16 | 16.6 | 14.8
9 | 16.9 | 17.5 | 17.1
10 | 18.3 | 18.3 | 18.6
11 | 20 | 19.1 | 20.2
12 | 20.4 | 19.7 | 21.8
13 | 21.3 | 20.1 | 21.5
14 | 21.9 | 20.4 | 22.6
15 | 21.9 | 20.7 | 22.9
16 | 21.2 | 20.3 | 23.3
17 | 21.1 | 20 | 22.8
18 | 20.1 | 19.4 | 21.7
19 | 18.3 | 18.6 | 19.5
20 | 17.9 | 17.6 | 18.2
21 | 16.5 | 16.5 | 15.8
22 | 15.2 | 15.6 | 12.7
23 | 15.5 | 15 | 12.9
0 | 15.7 | 11.9 | 13.1
1 | 14.6 | 11 | 11
2 | 13.8 | 10.5 | 9.2
3 | 13.8 | 9.9 | 9.1
4 | 13.8 | 9.9 | 9
5 | 13.8 | 10.4 | 9.6
6 | 13.9 | 11.9 | 10.1
7 | 16.7 | 13.7 | 13.2
8 | 19.2 | 15.4 | 16.1
9 | 20.6 | 17 | 19
10 | 22.3 | 18.4 | 21.5
11 | 23.5 | 19.6 | 22.8
12 | 22.8 | 20.6 | 24
13 | 24.7 | 21.4 | 26
14 | 25.4 | 21.9 | 26.7
15 | 25.5 | 22.3 | 27
16 | 25.4 | 21.7 | 26
17 | 25.1 | 21.1 | 25.4
18 | 24.3 | 20.2 | 25.1
19 | 22 | 18.9 | 23.1
20 | 20.4 | 17.1 | 19.7
21 | 18.7 | 15.3 | 16.6
22 | 16.4 | 13.8 | 14.7
23 | 16.1 | 12.8 | 14.4
0 | 15.7 | 11.6 | 14.1
1 | 12.9 | 10.8 | 13
2 | 10.9 | 10.2 | 12.1
3 | 11 | 9.7 | 12.1
4 | 10.9 | 9.7 | 12.1
5 | 11.4 | 10.2 | 12.6
6 | 12 | 11.6 | 13.1
7 | 13.7 | 13.3 | 15.7
8 | 16.5 | 15 | 17.9
9 | 19.1 | 16.4 | 20.2
10 | 20.7 | 17.8 | 22.1
11 | 22.4 | 19 | 23.8
12 | 22.3 | 19.9 | 25.9
13 | 24.1 | 20.7 | 25.5
14 | 24.3 | 21.2 | 26.3
15 | 24.3 | 21.5 | 26.8
16 | 25 | 21 | 26
17 | 25 | 20.4 | 25.9
18 | 22.4 | 19.6 | 25.3
19 | 21.2 | 18.3 | 22.6
20 | 19 | 16.6 | 20.5
21 | 16.7 | 14.9 | 18.1
22 | 14.7 | 13.4 | 16.9
23 | 14.9 | 12.5 | 15.6
0 | 15.1 | 13.8 | 14.4
1 | 13.7 | 13.1 | 11.3
2 | 12.9 | 12.7 | 9.2
3 | 12.8 | 12.3 | 9.2
4 | 12.7 | 12.3 | 9.2
5 | 12.9 | 12.6 | 9.6
6 | 13.1 | 13.8 | 10.1
7 | 14.4 | 15.2 | 11.9
8 | 16 | 16.5 | 14.6
9 | 17.1 | 17.7 | 17
10 | 18.3 | 18.8 | 19
11 | 19.3 | 19.7 | 20.2
12 | 19.8 | 20.5 | 22.2
13 | 20.1 | 21.1 | 22
14 | 20.6 | 21.5 | 22.7
15 | 20.3 | 21.8 | 23.5
16 | 20 | 21.3 | 23.5
17 | 18.9 | 20.9 | 21.9
18 | 19.3 | 20.2 | 21.2
19 | 19 | 19.2 | 20
20 | 17.4 | 17.8 | 17.2
21 | 15.8 | 16.4 | 15.2
22 | 14.8 | 15.2 | 13.8
23 | 14.3 | 13.1 | 13.5
0 | 13.8 | 11 | 13.2
1 | 13.2 | 8.9 | 12.9
2 | 12.7 | 6.8 | 12.6
3 | 12 | 6.3 | 12.5
4 | 12.2 | 6.1 | 12.6
5 | 12.3 | 6.5 | 12.7
6 | 12.7 | 7.8 | 12.8
7 | 13.6 | 9.5 | 14.1
8 | 15 | 11.2 | 15.3
9 | 16.2 | 12.8 | 16
10 | 17.8 | 14.2 | 17.8
11 | 19.3 | 15.6 | 18.3
12 | 19.1 | 16.7 | 19.1
13 | 20.2 | 17.4 | 19.5
14 | 20 | 17.9 | 19.8
15 | 20.6 | 18.1 | 19.5
16 | 20 | 17.7 | 19.9
17 | 19.5 | 17.1 | 19.5
18 | 18.8 | 16.2 | 18.9
19 | 18.6 | 14.8 | 17.7
20 | 17.2 | 13.1 | 17.2
21 | 15.7 | 11.3 | 15.9
22 | 14.5 | 9.8 | 14.6
23 | 14.9 | 8.7 | 14.8
0 | 15.4 | 8.7 | 15
1 | 14.9 | 8.1 | 13.8
2 | 14.5 | 7.7 | 13.1
3 | 14.7 | 7.3 | 12.8
4 | 14.7 | 7.1 | 12.7
5 | 14.5 | 7.4 | 12.7
6 | 14.3 | 8.5 | 13.6
7 | 14.7 | 10 | 14.6
8 | 15.2 | 11.5 | 17
9 | 15.5 | 12.9 | 17.4
10 | 15.8 | 14.2 | 19
11 | 16.6 | 15.3 | 20.1
12 | 16.7 | 16.3 | 21
13 | 16.5 | 16.9 | 21.8
14 | 16.8 | 17.4 | 22
15 | 17.1 | 17.5 | 22.4
16 | 16.7 | 17.2 | 21.8
17 | 16.8 | 16.6 | 22
18 | 16.1 | 15.8 | 20.6
19 | 16.4 | 14.7 | 20.3
20 | 15.8 | 13.1 | 18.1
21 | 15.2 | 11.6 | 16.7
22 | 14.5 | 10.3 | 16.1
23 | 15.9 | 9.4 | 15.1
0 | 17.4 | 11.5 | 14.1
1 | 17.5 | 10.8 | 11.5
2 | 17.6 | 10.3 | 9.6
3 | 17.5 | 9.9 | 9.4
4 | 17.4 | 9.7 | 9.3
5 | 17.6 | 10.1 | 9.5
6 | 17.9 | 11.3 | 9.9
7 | 17.7 | 13 | 12.4
8 | 17.6 | 14.8 | 14.4
9 | 18.1 | 16.3 | 17
10 | 18.2 | 17.7 | 19.1
11 | 18.5 | 19.1 | 19.9
12 | 18.8 | 20.1 | 21.4
13 | 18.4 | 20.9 | 21.4
14 | 18.8 | 21.4 | 23
15 | 18.6 | 21.6 | 23.1
16 | 18.3 | 21.2 | 21.9
17 | 18.6 | 20.5 | 21.9
18 | 18.3 | 19.6 | 20.9
19 | 18.7 | 18.3 | 19.2
20 | 17.7 | 16.6 | 17.1
21 | 18 | 14.8 | 15.2
22 | 17.9 | 13.3 | 13.6
23 | 18.3 | 12.3 | 15.2
0 | 18.7 | 13.5 | 16.8
1 | 18.5 | 12.7 | 17
2 | 18.4 | 12.1 | 17.1
3 | 18.7 | 11.6 | 17
4 | 18.5 | 11.3 | 16.8
5 | 18.4 | 11.8 | 17.1
6 | 18.6 | 13.3 | 17.3
7 | 18.8 | 15.4 | 17.6
8 | 19.4 | 17.5 | 18.5
9 | 20.7 | 19.3 | 19
10 | 21.6 | 21.1 | 20.1
11 | 21.7 | 22.7 | 20.7
12 | 22.6 | 24 | 20.5
13 | 22 | 24.9 | 21
14 | 22.2 | 25.5 | 21.2
15 | 22.3 | 25.7 | 20.5
16 | 22.6 | 25.2 | 20.6
17 | 22 | 24.5 | 20.8
18 | 22.1 | 23.4 | 21
19 | 21.1 | 21.8 | 19.8
20 | 20.7 | 19.7 | 19.5
21 | 19.7 | 17.5 | 18.1
22 | 19.6 | 15.7 | 18.1
23 | 19 | 14.5 | 18.3
0 | 18.5 | 16.6 | 18.4
1 | 15.4 | 16 | 17.9
2 | 13.3 | 15.6 | 17.4
3 | 13.1 | 15.2 | 17.4
4 | 13 | 15 | 17.3
5 | 13 | 15.3 | 17.5
6 | 13.2 | 16.4 | 17.6
7 | 15 | 17.9 | 19.3
8 | 16.5 | 19.4 | 21.1
9 | 17.7 | 20.8 | 22.1
10 | 19.3 | 22 | 23.6
11 | 20.7 | 23.2 | 24.9
12 | 22.2 | 24.1 | 25.4
13 | 22 | 24.8 | 26.2
14 | 22.2 | 25.2 | 25.8
15 | 22.1 | 25.4 | 26.4
16 | 23 | 25 | 26.3
17 | 22.4 | 24.4 | 25.1
18 | 21.5 | 23.7 | 24.9
19 | 20.1 | 22.5 | 24
20 | 18.5 | 21 | 22.4
21 | 16.7 | 19.4 | 21.1
22 | 15.8 | 18.2 | 20.3
23 | 16.2 | 17.3 | 19.7
0 | 16.5 | 15.8 | 19.1
1 | 15.7 | 15.4 | 16.9
2 | 15.3 | 15.2 | 15.5
3 | 15.3 | 14.9 | 15.5
4 | 15.1 | 14.8 | 15.5
5 | 15.2 | 15 | 15.7
6 | 15.3 | 15.7 | 16
7 | 16.6 | 16.7 | 16.4
8 | 18.5 | 17.7 | 17
9 | 19.8 | 18.5 | 17.5
10 | 20.2 | 19.3 | 18.8
11 | 20.4 | 20.1 | 19.2
12 | 21.3 | 20.7 | 19.1
13 | 22.6 | 21.1 | 19.6
14 | 22.8 | 21.4 | 20.1
15 | 22.5 | 21.5 | 19.8
16 | 22.2 | 21.3 | 20
17 | 22.1 | 20.9 | 19.3
18 | 21.6 | 20.4 | 19.3
19 | 20.4 | 19.7 | 18.5
20 | 19.5 | 18.7 | 17.9
21 | 18.6 | 17.7 | 17.3
22 | 17.8 | 16.8 | 16.7
23 | 17.6 | 16.3 | 16.9
0 | 17.4 | 14.6 | 17
1 | 15.3 | 14.2 | 16.1
2 | 13.7 | 14 | 15.7
3 | 13.5 | 13.7 | 15.4
4 | 13.5 | 13.6 | 15.5
5 | 13.8 | 13.8 | 15.6
6 | 14.2 | 14.5 | 15.7
7 | 16.2 | 15.5 | 16.7
8 | 18.6 | 16.4 | 17.3
9 | 20.3 | 17.3 | 18.2
10 | 21.7 | 18.1 | 19.2
11 | 23.8 | 18.8 | 20.4
12 | 24.6 | 19.4 | 20.4
13 | 25.2 | 19.9 | 20.9
14 | 25.1 | 20.1 | 21.1
15 | 25.9 | 20.2 | 21.4
16 | 25.1 | 20 | 20.9
17 | 25.2 | 19.7 | 21.2
18 | 23.8 | 19.2 | 20.7
19 | 23.1 | 18.4 | 19.8
20 | 20.3 | 17.4 | 18.7
21 | 17.9 | 16.4 | 17.7
22 | 16.5 | 15.6 | 17.4
23 | 16.3 | 15.1 | 17.4
0 | 16 | 14.6 | 17.3
1 | 13.1 | 14.1 | 15.7
2 | 11.2 | 13.7 | 14.7
3 | 11.2 | 13.4 | 14.7
4 | 11.2 | 13.2 | 14.6
5 | 11.2 | 13.5 | 14.6
6 | 11.2 | 14.5 | 15.1
7 | 13.4 | 15.8 | 15.7
8 | 14.5 | 17.1 | 16.2
9 | 15.4 | 18.3 | 17.6
10 | 17.3 | 19.4 | 18.6
11 | 18.2 | 20.5 | 18.6
12 | 18.7 | 21.3 | 19.6
13 | 20.1 | 21.9 | 19.5
14 | 19.5 | 22.3 | 20.1
15 | 20.1 | 22.4 | 19.7
16 | 20.1 | 22.1 | 19.6
17 | 19 | 21.6 | 20.1
18 | 18.8 | 20.9 | 20.1
19 | 18.3 | 19.9 | 18
20 | 15.7 | 18.5 | 17.9
21 | 14.5 | 17.2 | 16.5
22 | 13.7 | 16 | 16.1
23 | 16.4 | 15.2 | 16.1
0 | 19.2 | 16 | 16.1
1 | 19.3 | 15.6 | 14.6
2 | 19.4 | 15.4 | 13.7
3 | 19.3 | 15.2 | 13.6
4 | 19.2 | 15 | 13.5
5 | 19.5 | 15.2 | 13.5
6 | 19.7 | 15.9 | 13.6
7 | 20.9 | 16.8 | 13.8
8 | 22.7 | 17.7 | 14.4
9 | 23.2 | 18.5 | 15.4
10 | 25.4 | 19.3 | 15.7
11 | 25.6 | 19.9 | 16.7
12 | 26.4 | 20.5 | 16.5
13 | 26.6 | 20.9 | 16.2
14 | 26.4 | 21.2 | 16.4
15 | 27 | 21.3 | 16.3
16 | 26.4 | 21 | 16.9
17 | 26.6 | 20.7 | 16.5
18 | 25.9 | 20.2 | 16.3
19 | 24.3 | 19.6 | 15.7
20 | 23.6 | 18.7 | 15.1
21 | 21.9 | 17.7 | 15.1
22 | 21.4 | 16.9 | 14.5
23 | 22.2 | 16.4 | 15.7
0 | 23 | 13.1 | 16.9
1 | 22.6 | 12.5 | 17
2 | 22.4 | 12.1 | 17.1
3 | 22.2 | 11.8 | 16.9
4 | 22 | 11.6 | 16.9
5 | 22.1 | 11.9 | 16.9
6 | 22.1 | 12.9 | 17.7
7 | 22.9 | 14.4 | 18.5
8 | 23.4 | 15.8 | 19.9
9 | 24.1 | 17 | 21
10 | 25.9 | 18.2 | 22.5
11 | 26.6 | 19.3 | 23.8
12 | 26.6 | 20.2 | 24.6
13 | 26.6 | 20.9 | 25.3
14 | 26.7 | 21.2 | 24.8
15 | 26.8 | 21.4 | 25.2
16 | 27.1 | 21.1 | 25.4
17 | 26.2 | 20.5 | 24.9
18 | 26.5 | 19.8 | 24.6
19 | 25.6 | 18.7 | 23.1
20 | 24.9 | 17.3 | 21.9
21 | 23.8 | 15.8 | 21
22 | 23.7 | 14.6 | 19.5
23 | 24.2 | 13.7 | 19.5
0 | 24.7 | 15.5 | 19.5
1 | 24.5 | 14.9 | 18.4
2 | 24.4 | 14.4 | 17.8
3 | 24.4 | 14 | 17.6
4 | 24.2 | 13.8 | 17.5
5 | 23.9 | 14.2 | 17.5
6 | 24.1 | 15.3 | 17.5
7 | 24.2 | 16.9 | 18.5
8 | 24.5 | 18.5 | 19
9 | 25.2 | 19.9 | 19.2
10 | 25.4 | 21.2 | 19.8
11 | 25.7 | 22.4 | 20.6
12 | 26 | 23.4 | 20.6
13 | 26.2 | 24.1 | 20.7
14 | 25.5 | 24.5 | 20.5
15 | 25.8 | 24.7 | 20.6
16 | 25.9 | 24.3 | 20.8
17 | 26 | 23.7 | 21
18 | 26.2 | 22.9 | 20.1
19 | 25.6 | 21.7 | 20
20 | 24.8 | 20.1 | 19.3
21 | 24.5 | 18.5 | 18.8
22 | 24.8 | 17.2 | 18
23 | 24.3 | 16.2 | 17.7
0 | 23.8 | 13.2 | 17.5
1 | 21.9 | 12.4 | 15.1
2 | 21.3 | 11.8 | 13.3
3 | 20.7 | 11.2 | 13.3
4 | 20.8 | 10.9 | 13.3
5 | 21 | 11.4 | 13.3
6 | 20.7 | 13 | 13.4
7 | 21.7 | 15.2 | 14.7
8 | 23.2 | 17.4 | 15.8
9 | 23.7 | 19.4 | 17.4
10 | 24.6 | 21.2 | 17.9
11 | 25.3 | 22.9 | 19.7
12 | 25.6 | 24.3 | 20.5
13 | 26.2 | 25.3 | 20.6
14 | 26.7 | 25.9 | 21.4
15 | 25.9 | 26.1 | 20.6
16 | 26.1 | 25.6 | 20.8
17 | 26.1 | 24.8 | 21
18 | 25.9 | 23.7 | 20.8
19 | 25.1 | 22 | 19.4
20 | 23.8 | 19.8 | 17.6
21 | 22.8 | 17.5 | 16.6
22 | 22.3 | 15.6 | 15.8
23 | 21.8 | 14.3 | 16.2
0 | 21.2 | 17.3 | 16.5
1 | 17.9 | 16.9 | 15.4
2 | 15.5 | 16.6 | 14.8
3 | 15.5 | 16.3 | 14.5
4 | 15.5 | 16.1 | 14.4
5 | 15.5 | 16.4 | 14.3
6 | 15.7 | 17.2 | 14.6
7 | 18 | 18.4 | 14.9
8 | 19.8 | 19.6 | 16.6
9 | 22.1 | 20.6 | 17.4
10 | 24.1 | 21.6 | 18.5
11 | 25 | 22.5 | 18.5
12 | 26.2 | 23.2 | 19.3
13 | 26.6 | 23.7 | 19.7
14 | 27.3 | 24 | 20.1
15 | 26.6 | 24.2 | 19.5
16 | 26.4 | 23.9 | 19.7
17 | 25.2 | 23.5 | 19.7
18 | 25.5 | 22.9 | 19.8
19 | 24.2 | 22 | 18.6
20 | 22.6 | 20.8 | 17.3
21 | 20.3 | 19.6 | 16
22 | 18.1 | 18.6 | 16.3
23 | 17.8 | 17.9 | 16.1
0 | 17.5 | 17.7 | 15.9
1 | 14.9 | 17.4 | 14.1
2 | 13.1 | 17.3 | 12.9
3 | 13.1 | 17.1 | 12.8
4 | 13 | 17 | 12.8
5 | 13 | 17.2 | 12.8
6 | 13.1 | 17.6 | 12.8
7 | 15.9 | 18.2 | 14.9
8 | 18 | 18.8 | 16.5
9 | 20.4 | 19.3 | 18.9
10 | 22.4 | 19.8 | 19.6
11 | 23.6 | 20.3 | 20.8
12 | 24.4 | 20.7 | 21.5
13 | 25.4 | 20.9 | 22.4
14 | 26 | 21.1 | 22.9
15 | 26.3 | 21.2 | 23.2
16 | 26.4 | 21 | 22.9
17 | 26 | 20.8 | 22.8
18 | 24.7 | 20.5 | 22
19 | 22.9 | 20 | 20.2
20 | 20.7 | 19.4 | 18.7
21 | 18.3 | 18.8 | 17.9
22 | 17.4 | 18.3 | 16
23 | 16.7 | 17.9 | 15.4
0 | 16 | 16.2 | 14.8
1 | 14.1 | 16 | 12.5
2 | 12.6 | 15.8 | 10.8
3 | 12.4 | 15.7 | 10.5
4 | 12.2 | 15.6 | 10.3
5 | 12.4 | 15.7 | 10.6
6 | 12.5 | 16.1 | 11
7 | 15 | 16.6 | 13.7
8 | 17.1 | 17.1 | 15.6
9 | 19.4 | 17.6 | 17.7
10 | 20.4 | 18 | 20.2
11 | 22.3 | 18.4 | 21.7
12 | 23.3 | 18.7 | 22
13 | 24.3 | 19 | 23.2
14 | 24 | 19.1 | 24.3
15 | 24.3 | 19.2 | 24.7
16 | 24.8 | 19 | 24.3
17 | 23.2 | 18.9 | 23.9
18 | 22.1 | 18.6 | 22.1
19 | 21.5 | 18.2 | 21.8
20 | 19.9 | 17.7 | 18.8
21 | 17.3 | 17.1 | 17
22 | 15.9 | 16.7 | 14.6
23 | 15.6 | 16.4 | 14.6
0 | 15.2 | 13.1 | 14.6
1 | 13.2 | 12.6 | 14.2
2 | 11.8 | 12.2 | 14
3 | 11.6 | 11.9 | 13.8
4 | 11.4 | 11.4 | 13.8
5 | 11.4 | 11.8 | 13.8
6 | 11.5 | 12.7 | 14
7 | 13.7 | 14.2 | 14.3
8 | 15.7 | 15.8 | 16.6
9 | 17.8 | 17.3 | 17.1
10 | 19.3 | 18.7 | 18.3
11 | 20.5 | 19.9 | 19.2
12 | 21.3 | 20.9 | 19.2
13 | 22.2 | 21.6 | 20.2
14 | 22.2 | 22.2 | 20.4
15 | 21.8 | 22.2 | 20.3
16 | 22.5 | 22 | 20.2
17 | 22.1 | 21.4 | 19.8
18 | 20.2 | 20.5 | 20.1
19 | 19.4 | 19.2 | 18.3
20 | 17.4 | 17.5 | 17.4
21 | 15.3 | 15.9 | 16.3
22 | 14.6 | 14.7 | 15.9
23 | 15.3 | 13.8 | 16.1
0 | 15.9 | 13.2 | 16.3
1 | 15.6 | 13 | 15.4
2 | 15.3 | 12.7 | 14.7
3 | 15.5 | 12.5 | 14.6
4 | 15.7 | 12.3 | 14.4
5 | 15.4 | 12.5 | 14.6
6 | 15.7 | 13 | 14.7
7 | 16.7 | 13.9 | 16.6
8 | 17.9 | 14.8 | 17.9
9 | 19.3 | 15.6 | 20
10 | 19.7 | 16.4 | 20.9
11 | 21 | 17.1 | 22.2
12 | 21.6 | 17.6 | 23
13 | 21.7 | 18 | 23.8
14 | 21.9 | 18.3 | 24.3
15 | 22.2 | 18.4 | 24
16 | 21.7 | 18.3 | 24.5
17 | 21.9 | 17.9 | 24
18 | 20.9 | 17.4 | 23.8
19 | 20.1 | 16.7 | 22.2
20 | 18.4 | 15.7 | 19.9
21 | 18.3 | 14.8 | 18.6
22 | 17.4 | 14.1 | 17
23 | 17.2 | 13.6 | 16.6
0 | 17.1 | 12.6 | 16.3
1 | 15.4 | 12.1 | 14
2 | 14.2 | 11.7 | 12
3 | 14.5 | 11.3 | 11.9
4 | 14.3 | 10.9 | 11.9
5 | 14.1 | 11.2 | 12.2
6 | 15.2 | 12.2 | 12.6
7 | 16.3 | 13.7 | 15
8 | 16.3 | 15.4 | 18.3
9 | 18.9 | 16.9 | 20.3
10 | 19.8 | 18.3 | 21.9
11 | 20.6 | 19.6 | 25.1
12 | 21.4 | 20.6 | 25.3
13 | 22.1 | 21.4 | 26.9
14 | 21.7 | 21.9 | 27.8
15 | 22.5 | 22 | 27.2
16 | 21.8 | 21.8 | 27.5
17 | 21.8 | 21.1 | 27.9
18 | 21.4 | 20.2 | 25.7
19 | 19.9 | 18.8 | 24.1
20 | 19.2 | 17.1 | 20.8
21 | 16.9 | 15.5 | 18.5
22 | 16.5 | 14.2 | 16.8
23 | 16.6 | 13.3 | 16.1
0 | 16.7 | 15.9 | 15.3
1 | 15.1 | 15.8 | 13.2
2 | 13.9 | 15.6 | 11.8
3 | 13.9 | 15.4 | 11.8
4 | 13.7 | 15.3 | 11.7
5 | 14 | 15.4 | 11.7
6 | 14.3 | 15.8 | 12.3
7 | 16 | 16.4 | 13
8 | 17.9 | 17 | 14
9 | 19.3 | 17.6 | 15.8
10 | 20.4 | 18.1 | 17.2
11 | 22 | 18.6 | 17.9
12 | 23.3 | 19 | 18
13 | 23.5 | 19.3 | 18.4
14 | 23.6 | 19.5 | 18.7
15 | 23.8 | 19.5 | 19.2
16 | 22.9 | 19.5 | 19.3
17 | 24.1 | 19.2 | 18.5
18 | 22.1 | 18.9 | 18.2
19 | 21.3 | 18.3 | 17.6
20 | 20.1 | 17.7 | 16.1
21 | 18.2 | 17 | 14.8
22 | 16.8 | 16.6 | 13.7
23 | 17.3 | 16.2 | 13.4
0 | 17.8 | 12.5 | 13.1
1 | 17.7 | 12 | 11.3
2 | 17.6 | 11.6 | 9.9
3 | 17.9 | 11.2 | 9.9
4 | 17.7 | 10.7 | 9.7
5 | 17.4 | 11.1 | 9.6
6 | 18.5 | 12.1 | 10.9
7 | 19.6 | 13.8 | 12.2
8 | 20.8 | 15.7 | 14.8
9 | 22.2 | 17.3 | 16.6
10 | 24.4 | 18.8 | 18.6
11 | 24.4 | 20.2 | 19.7
12 | 26.6 | 21.3 | 21.4
13 | 26.3 | 22.2 | 22.1
14 | 26.9 | 22.7 | 23.1
15 | 26.7 | 22.8 | 22.9
16 | 26.4 | 22.6 | 23.2
17 | 26.3 | 21.9 | 22.3
18 | 25.5 | 20.9 | 22.6
19 | 24.4 | 19.4 | 19.7
20 | 22.6 | 17.6 | 17.3
21 | 21 | 15.7 | 15.3
22 | 20.3 | 14.4 | 14.1
23 | 20.6 | 13.3 | 13.1
0 | 21 | 12.3 | 12
1 | 20 | 12 | 9.9
2 | 19.5 | 11.7 | 7.9
3 | 19 | 11.5 | 7.8
4 | 19.1 | 11.2 | 7.8
5 | 19.2 | 11.4 | 8.3
6 | 19.3 | 12.1 | 8.7
7 | 19.9 | 13.1 | 10.8
8 | 21.3 | 14.2 | 13.1
9 | 22.4 | 15.2 | 15.4
10 | 23.2 | 16.2 | 17.1
11 | 24.6 | 17 | 18.3
12 | 25.1 | 17.7 | 20.2
13 | 25.3 | 18.2 | 20.9
14 | 25.6 | 18.6 | 21.9
15 | 25.9 | 18.6 | 21.3
16 | 25.6 | 18.5 | 21.9
17 | 25.6 | 18.1 | 20.8
18 | 25.9 | 17.4 | 19.7
19 | 24.4 | 16.5 | 18.1
20 | 23 | 15.4 | 15.8
21 | 21.4 | 14.3 | 13.8
22 | 20.6 | 13.4 | 13.1
23 | 20.1 | 12.8 | 12.7
0 | 19.6 | 15.7 | 12.4
1 | 16.5 | 15.4 | 11.7
2 | 14.4 | 15.2 | 11
3 | 14.2 | 14.9 | 10.8
4 | 14.1 | 14.7 | 10.8
5 | 14.3 | 14.9 | 10.8
6 | 14.6 | 15.5 | 11.4
7 | 16.3 | 16.4 | 12
8 | 18 | 17.4 | 13.6
9 | 20.1 | 18.3 | 15.1
10 | 21.8 | 19.2 | 15.8
11 | 23.3 | 19.9 | 16.4
12 | 24.3 | 20.5 | 16.9
13 | 24.2 | 21 | 17.6
14 | 25.5 | 21.3 | 18.3
15 | 25 | 21.4 | 17.8
16 | 25 | 21.2 | 17.8
17 | 24.9 | 20.9 | 18.1
18 | 23.8 | 20.3 | 17.1
19 | 22.5 | 19.5 | 17
20 | 20 | 18.5 | 14.5
21 | 18.3 | 17.5 | 14.4
22 | 17.3 | 16.7 | 13.1
23 | 17.8 | 16.1 | 12.9
0 | 18.2 | 13.2 | 12.7
1 | 18.1 | 12.8 | 11
2 | 17.9 | 12.5 | 9.9
3 | 17.6 | 12.2 | 9.5
4 | 17.7 | 11.9 | 9.1
5 | 17.8 | 12.1 | 9.2
6 | 17.9 | 12.9 | 9.4
7 | 18.7 | 14.2 | 10.9
8 | 20 | 15.5 | 13.2
9 | 21 | 16.7 | 15.2
10 | 21.8 | 17.8 | 16.3
11 | 22.7 | 18.8 | 17.7
12 | 23.2 | 19.6 | 19
13 | 23.7 | 20.3 | 19.8
14 | 23.7 | 20.7 | 19.7
15 | 24 | 20.7 | 19.5
16 | 23.7 | 20.6 | 20.1
17 | 23.8 | 20.1 | 19.3
18 | 22.7 | 19.3 | 17.8
19 | 22.7 | 18.2 | 17.2
20 | 20.5 | 16.9 | 15.4
21 | 20.1 | 15.5 | 13.9
22 | 19.4 | 14.6 | 12.6
23 | 18.9 | 13.8 | 12.3
0 | 18.5 | 12.8 | 11.9
1 | 15.3 | 12.4 | 10.3
2 | 13.1 | 12.1 | 9
3 | 12.9 | 11.8 | 9.3
4 | 12.9 | 11.4 | 9.1
5 | 13.1 | 11.7 | 9
6 | 13.6 | 12.5 | 9.6
7 | 15.8 | 13.8 | 10.3
8 | 17.5 | 15.2 | 11.7
9 | 20.8 | 16.5 | 12.8
10 | 21.7 | 17.7 | 14.2
11 | 23.9 | 18.7 | 16
12 | 25.1 | 19.6 | 16.6
13 | 25.5 | 20.2 | 16
14 | 26.5 | 20.7 | 16.8
15 | 25.8 | 20.7 | 16.7
16 | 25.9 | 20.6 | 17.2
17 | 25.8 | 20 | 16.6
18 | 24.1 | 19.2 | 15.8
19 | 22.6 | 18.1 | 15.2
20 | 20.6 | 16.7 | 14.1
21 | 17.8 | 15.3 | 12.5
22 | 16.3 | 14.2 | 11.6
23 | 17 | 13.4 | 13.3
0 | 17.7 | 13.8 | 14.9
1 | 16.9 | 13.4 | 15.1
2 | 16.5 | 13.1 | 15.2
3 | 16 | 12.8 | 15.1
4 | 16.2 | 12.4 | 14.9
5 | 16.3 | 12.7 | 15
6 | 16.5 | 13.5 | 15
7 | 18.9 | 14.8 | 15.6
8 | 20.9 | 16.2 | 16.8
9 | 22.8 | 17.5 | 17.9
10 | 23.7 | 18.7 | 19.4
11 | 25.7 | 19.8 | 19.5
12 | 26.9 | 20.6 | 20.3
13 | 26.9 | 21.3 | 20.4
14 | 28.3 | 21.7 | 20.4
15 | 28 | 21.8 | 20.7
16 | 27.5 | 21.6 | 20.4
17 | 27.8 | 21.1 | 20.2
18 | 27.6 | 20.3 | 19.8
19 | 25.4 | 19.1 | 19.7
20 | 22.9 | 17.7 | 18.9
21 | 21.5 | 16.3 | 16.6
22 | 19.8 | 15.2 | 16.6
23 | 19.8 | 14.4 | 16.3
0 | 19.7 | 14.9 | 16
1 | 18.6 | 14.6 | 14
2 | 18 | 14.4 | 12.5
3 | 17.3 | 14.2 | 12.2
4 | 17.4 | 13.9 | 12
5 | 17.5 | 14.1 | 12.1
6 | 17.7 | 14.7 | 12.3
7 | 19.9 | 15.6 | 14.2
8 | 23.1 | 16.6 | 16.6
9 | 25.1 | 17.4 | 18.1
10 | 27 | 18.2 | 20.1
11 | 29 | 19 | 20.5
12 | 29.9 | 19.6 | 21.9
13 | 30.4 | 20 | 23
14 | 30.5 | 20.3 | 23.6
15 | 30.8 | 20.4 | 22.9
16 | 31.2 | 20.2 | 23.2
17 | 30.2 | 19.9 | 22.8
18 | 29.3 | 19.3 | 22.4
19 | 27.3 | 18.5 | 20.4
20 | 25.3 | 17.6 | 18.7
21 | 23.3 | 16.6 | 17.1
22 | 21.2 | 15.9 | 15.5
23 | 20.8 | 15.3 | 15.8
0 | 20.4 | 14.6 | 16.1
1 | 18.3 | 14.1 | 15.6
2 | 17.5 | 13.7 | 15.4
3 | 16.8 | 13.4 | 15.3
4 | 16.9 | 12.9 | 15.3
5 | 17 | 13.3 | 15.2
6 | 17.6 | 14.2 | 15.7
7 | 19 | 15.7 | 16.3
8 | 20.4 | 17.3 | 17.5
9 | 21.9 | 18.8 | 18.3
10 | 23.3 | 20.1 | 18.4
11 | 24.6 | 21.3 | 18.9
12 | 26 | 22.3 | 19.8
13 | 26.3 | 23 | 20.1
14 | 26.5 | 23.5 | 20
15 | 26.9 | 23.6 | 20
16 | 26.4 | 23.4 | 20.5
17 | 26.4 | 22.8 | 20.4
18 | 25.6 | 21.9 | 19.6
19 | 23.7 | 20.6 | 19
20 | 22.7 | 19 | 18.2
21 | 20.7 | 17.4 | 17.5
22 | 19.2 | 16.2 | 16.8
23 | 19.2 | 15.2 | 16.7
0 | 19.2 | 12.9 | 16.6
1 | 17.6 | 12.3 | 15
2 | 16.5 | 11.9 | 14
3 | 16.4 | 11.4 | 14.3
4 | 16.4 | 10.9 | 14.1
5 | 16.5 | 11.3 | 14
6 | 16.7 | 12.4 | 14
7 | 18.2 | 14.2 | 14.1
8 | 18.5 | 16.1 | 15.4
9 | 19.8 | 17.8 | 16.1
10 | 21.9 | 19.4 | 16.4
11 | 22.2 | 20.8 | 17.4
12 | 23 | 22 | 17.8
13 | 23.6 | 22.9 | 17.8
14 | 23.3 | 23.5 | 18.1
15 | 23.2 | 23.5 | 17.8
16 | 23.7 | 23.3 | 17.7
17 | 23.4 | 22.6 | 17.5
18 | 22.8 | 21.5 | 17.6
19 | 21.6 | 20 | 16.8
20 | 20.5 | 18.1 | 16.4
21 | 19.1 | 16.2 | 15.5
22 | 18.5 | 14.8 | 15.2
23 | 18.1 | 13.7 | 15.1
0 | 17.6 | 13.9 | 14.9
1 | 15.4 | 13.6 | 13.3
2 | 13.8 | 13.3 | 12
3 | 13.8 | 13.1 | 12.1
4 | 13.7 | 12.8 | 12
5 | 13.7 | 13 | 12
6 | 14.4 | 13.7 | 13.2
7 | 15.2 | 14.7 | 14.5
8 | 16.9 | 15.9 | 16.4
9 | 17.8 | 16.9 | 18.2
10 | 19.2 | 17.9 | 21.5
11 | 19.8 | 18.7 | 22.1
12 | 21.4 | 19.4 | 22.5
13 | 22.1 | 20 | 23.9
14 | 21.5 | 20.3 | 23.5
15 | 22.1 | 20.4 | 24.5
16 | 22 | 20.2 | 24.5
17 | 21.3 | 19.8 | 23.9
18 | 21.3 | 19.2 | 23.7
19 | 19.9 | 18.2 | 20.6
20 | 17.8 | 17.1 | 19.3
21 | 17 | 15.9 | 17.4
22 | 15.8 | 15.1 | 15.9
23 | 15.6 | 14.4 | 15.8
0 | 15.5 | 14.6 | 15.7
1 | 13.3 | 14.5 | 14.6
2 | 11.6 | 14.3 | 13.7
3 | 11.1 | 14.2 | 13.6
4 | 11.1 | 14.1 | 13.6
5 | 11.1 | 14.2 | 13.7
6 | 12.5 | 14.5 | 13.8
7 | 13.9 | 15 | 15.9
8 | 16 | 15.6 | 17.9
9 | 17.5 | 16.1 | 18.9
10 | 19 | 16.6 | 20.2
11 | 20.3 | 17 | 21.5
12 | 21.4 | 17.3 | 22.7
13 | 21.9 | 17.6 | 22.5
14 | 23.1 | 17.8 | 23.1
15 | 22.4 | 17.8 | 23.7
16 | 22.1 | 17.7 | 23.3
17 | 21.9 | 17.5 | 23.5
18 | 21.4 | 17.2 | 22.2
19 | 19.3 | 16.7 | 21
20 | 17.6 | 16.2 | 19.6
21 | 16.1 | 15.6 | 18.5
22 | 14.5 | 15.2 | 16.5
23 | 14.7 | 14.9 | 17.2
0 | 14.9 | 14.5 | 17.9
1 | 13.8 | 14 | 18
2 | 12.8 | 13.6 | 18
3 | 12.8 | 13.3 | 18.1
4 | 12.7 | 12.9 | 18
5 | 12.8 | 13.2 | 17.9
6 | 12.8 | 14.1 | 18.7
7 | 14.3 | 15.6 | 19.4
8 | 15.6 | 17.1 | 21.1
9 | 18.1 | 18.6 | 22.6
10 | 18.7 | 19.9 | 24.3
11 | 20.3 | 21 | 24.9
12 | 19.9 | 22 | 25.1
13 | 21 | 22.7 | 26.4
14 | 21.3 | 23.2 | 26.2
15 | 21.1 | 23.3 | 26.7
16 | 21 | 23.1 | 26.5
17 | 20.7 | 22.5 | 26.3
18 | 19.4 | 21.6 | 25.7
19 | 18.9 | 20.4 | 25
20 | 17.3 | 18.8 | 23.6
21 | 15.7 | 17.2 | 21.8
22 | 14.8 | 16 | 19.9
23 | 15.2 | 15 | 19.9
0 | 15.6 | 14 | 19.9
1 | 16 | 13 | 17.9
2 | 16.4 | 12 | 16.3
3 | 16.6 | 11.6 | 16
4 | 16.4 | 11 | 16
5 | 16.3 | 10.7 | 16
6 | 16.6 | 11.9 | 17.2
7 | 17 | 14 | 18.5
8 | 17.3 | 16.5 | 20.7
9 | 17.9 | 18.6 | 22.4
10 | 18.7 | 20.4 | 25
11 | 19.2 | 22 | 26.1
12 | 19.2 | 23.4 | 28.2
13 | 19.2 | 24.4 | 28
14 | 19.6 | 24.8 | 28.9
15 | 19.3 | 24.9 | 29.2
16 | 19.3 | 24.5 | 28.7
17 | 19.2 | 23.7 | 28.9
18 | 19.2 | 22.4 | 27.1
19 | 18.7 | 20.6 | 26
20 | 17.9 | 18.3 | 24.1
21 | 17.2 | 16.3 | 21.4
22 | 17.1 | 15 | 20.3
23 | 17.5 | 13.9 | 19
0 | 18 | 14.8 | 17.7
1 | 17.3 | 14.3 | 14.4
2 | 16.7 | 13.9 | 11.8
3 | 16.4 | 13.6 | 11.7
4 | 16.3 | 13.2 | 11.7
5 | 16.1 | 12.9 | 11.8
6 | 17.1 | 13.8 | 11.9
7 | 18 | 15.5 | 13.6
8 | 19.9 | 17.4 | 16.2
9 | 21.8 | 19.1 | 18.2
10 | 23.4 | 20.4 | 20.4
11 | 24.9 | 21.7 | 21.5
12 | 25.7 | 22.7 | 22.1
13 | 26.7 | 23.5 | 23.7
14 | 26 | 23.8 | 23.6
15 | 26.4 | 23.9 | 24.3
16 | 26.2 | 23.6 | 24.2
17 | 26.2 | 22.9 | 23.2
18 | 25.1 | 22 | 22.5
19 | 23.5 | 20.6 | 20.4
20 | 21.1 | 18.8 | 19
21 | 20.2 | 17.3 | 16.8
22 | 18.8 | 16.2 | 15.5
23 | 19.6 | 15.5 | 15.8
0 | 20.4 | 15.7 | 16.1
1 | 19.8 | 15.4 | 15.3
2 | 19.3 | 15.2 | 14.9
3 | 19.3 | 15 | 14.4
4 | 19.2 | 14.7 | 14
5 | 19.1 | 14.5 | 14
6 | 19.8 | 15.1 | 14
7 | 20.5 | 16.1 | 15.4
8 | 21.7 | 17.3 | 17.5
9 | 23.8 | 18.4 | 18.7
10 | 25.2 | 19.2 | 20.5
11 | 26.7 | 20 | 21.4
12 | 26.2 | 20.7 | 22.5
13 | 27.6 | 21.1 | 22.5
14 | 27.1 | 21.4 | 22.9
15 | 27.6 | 21.4 | 23
16 | 27.1 | 21.2 | 23.4
17 | 27 | 20.8 | 22.6
18 | 26.9 | 20.2 | 22.1
19 | 25 | 19.3 | 21.1
20 | 23.7 | 18.2 | 19.4
21 | 22.1 | 17.3 | 18
22 | 21.8 | 16.6 | 16.9
23 | 21.4 | 16.1 | 17.3
0 | 21.1 | 14.8 | 17.7
1 | 19 | 14.4 | 17
2 | 17.6 | 14 | 16.5
3 | 16.8 | 13.7 | 16
4 | 16.7 | 13.3 | 15.9
5 | 16.7 | 13.1 | 15.8
6 | 17.4 | 13.9 | 16.5
7 | 18.1 | 15.4 | 17.3
8 | 20.3 | 17.1 | 19.1
9 | 22.3 | 18.6 | 20.2
10 | 24.6 | 19.9 | 22
11 | 26.1 | 21 | 23.2
12 | 26.5 | 21.9 | 23.9
13 | 26.9 | 22.6 | 25
14 | 27.1 | 22.9 | 24.6
15 | 27.6 | 23 | 24.9
16 | 27.6 | 22.7 | 24.8
17 | 26.7 | 22.1 | 24.5
18 | 25.4 | 21.3 | 23.9
19 | 24.2 | 20 | 22.2
20 | 22.1 | 18.4 | 20.7
21 | 20.9 | 17 | 19.7
22 | 20 | 16.1 | 18.4
23 | 20.1 | 15.4 | 18.7
0 | 20.2 | 15.3 | 19
1 | 19.2 | 14.8 | 18.2
2 | 18.4 | 14.4 | 17.6
3 | 17.6 | 14.1 | 17.7
4 | 17.5 | 13.7 | 17.6
5 | 17.4 | 13.4 | 17.5
6 | 18.1 | 14.3 | 17.4
7 | 18.8 | 16 | 18.9
8 | 21.1 | 17.8 | 20.3
9 | 23.1 | 19.4 | 20.8
10 | 24.3 | 20.8 | 22.6
11 | 25.6 | 22 | 23
12 | 26.2 | 23 | 23.9
13 | 27.4 | 23.7 | 24.8
14 | 27 | 24.1 | 24.4
15 | 27.7 | 24.2 | 24.5
16 | 26.9 | 23.8 | 24.1
17 | 27.1 | 23.2 | 24.6
18 | 26.2 | 22.3 | 24
19 | 24.6 | 20.9 | 22.9
20 | 23.3 | 19.2 | 21.4
21 | 21.5 | 17.7 | 19.8
22 | 20.5 | 16.7 | 19.9
23 | 19.9 | 15.9 | 18.8
0 | 19.3 | 10.8 | 17.8
1 | 16.8 | 10.3 | 14.3
2 | 14.8 | 9.9 | 11.7
3 | 14.3 | 9.6 | 11.6
4 | 13.9 | 9.1 | 11.2
5 | 14 | 8.9 | 10.9
6 | 14.2 | 9.8 | 12.6
7 | 16.7 | 11.6 | 14.5
8 | 19.5 | 13.6 | 17.6
9 | 22.6 | 15.3 | 20.9
10 | 24.9 | 16.7 | 23.5
11 | 27.1 | 18.1 | 25.2
12 | 28.8 | 19.2 | 27.4
13 | 29.3 | 19.9 | 29.2
14 | 30.4 | 20.3 | 28.9
15 | 29.9 | 20.4 | 29.7
16 | 29.6 | 20 | 29.2
17 | 29.2 | 19.4 | 28.5
18 | 27.9 | 18.4 | 26.4
19 | 25.7 | 16.9 | 23.5
20 | 22.8 | 15.1 | 21.5
21 | 20.9 | 13.4 | 18.7
22 | 18.8 | 12.3 | 16.3
23 | 18.7 | 11.5 | 16
0 | 18.6 | 14 | 15.6
1 | 16.6 | 13.8 | 13.5
2 | 15.3 | 13.6 | 11.8
3 | 14.6 | 13.5 | 11.3
4 | 14.4 | 13.3 | 10.8
5 | 14.4 | 13.2 | 10.9
6 | 15.7 | 13.6 | 11.1
7 | 17.2 | 14.2 | 13.8
8 | 18.9 | 15 | 16.4
9 | 22 | 15.7 | 18.9
10 | 23.7 | 16.2 | 21.7
11 | 26.1 | 16.7 | 23.3
12 | 26.8 | 17.1 | 25
13 | 27.5 | 17.4 | 26.3
14 | 28 | 17.6 | 26.3
15 | 28.4 | 17.6 | 26.8
16 | 28.1 | 17.5 | 25.7
17 | 27.9 | 17.2 | 26
18 | 26.5 | 16.8 | 24.1
19 | 23.8 | 16.3 | 22.3
20 | 22.2 | 15.6 | 19.8
21 | 19.7 | 14.9 | 17.4
22 | 18.4 | 14.5 | 15.7
23 | 17.6 | 14.2 | 15
0 | 16.8 | 12.2 | 14.3
1 | 13.9 | 11.9 | 11.9
2 | 12.1 | 11.7 | 10
3 | 11.2 | 11.5 | 9.9
4 | 11 | 11.3 | 9.6
5 | 11 | 11.1 | 9.5
6 | 12.1 | 11.7 | 10.5
7 | 13.3 | 12.6 | 11.5
8 | 16.5 | 13.8 | 14
9 | 19.6 | 14.8 | 16.3
10 | 21 | 15.6 | 18
11 | 22.9 | 16.3 | 19.6
12 | 24.1 | 16.9 | 19.9
13 | 25.4 | 17.4 | 21.4
14 | 26.1 | 17.6 | 21.5
15 | 25.6 | 17.6 | 21.6
16 | 25.2 | 17.4 | 22.1
17 | 24.1 | 17.1 | 21.4
18 | 23.6 | 16.5 | 20
19 | 21.7 | 15.6 | 18.7
20 | 18.7 | 14.6 | 16.3
21 | 17.2 | 13.7 | 14.8
22 | 15.9 | 13.1 | 13.5
23 | 15.8 | 12.6 | 14
0 | 15.8 | 10.4 | 14.5
1 | 15 | 10.1 | 14.5
2 | 14 | 9.8 | 14.3
3 | 13.8 | 9.6 | 13.9
4 | 13.6 | 9.3 | 13.5
5 | 13.7 | 9.2 | 13.6
6 | 13.7 | 9.8 | 13.7
7 | 15.8 | 10.8 | 14.9
8 | 17.8 | 12 | 16.7
9 | 20.1 | 13 | 18.3
10 | 21.6 | 13.9 | 19.4
11 | 23.7 | 14.6 | 20.1
12 | 24.9 | 15.3 | 20.9
13 | 25 | 15.7 | 21.5
14 | 24.8 | 16 | 22
15 | 25.6 | 16 | 21.5
16 | 25.2 | 15.8 | 22
17 | 24.5 | 15.4 | 21.4
18 | 23.7 | 14.8 | 20.6
19 | 22.5 | 13.9 | 19.4
20 | 19.9 | 12.9 | 18.6
21 | 18.1 | 11.9 | 16.9
22 | 17.1 | 11.2 | 16
23 | 17.1 | 10.8 | 15.3
0 | 17.2 | 12.1 | 14.6
1 | 15.5 | 11.8 | 12
2 | 14.1 | 11.6 | 10.1
3 | 13.8 | 11.4 | 10.2
4 | 13.8 | 11.1 | 9.8
5 | 13.7 | 11 | 9.5
6 | 14.3 | 11.5 | 10.5
7 | 15 | 12.5 | 11.6
8 | 17.8 | 13.6 | 14.1
9 | 19 | 14.5 | 16.4
10 | 20.4 | 15.3 | 18.1
11 | 21.3 | 16 | 19.6
12 | 22.4 | 16.6 | 20.8
13 | 23.4 | 17 | 21.9
14 | 23.8 | 17.3 | 22.5
15 | 23.5 | 17.3 | 22.5
16 | 23.2 | 17.1 | 22.6
17 | 23.4 | 16.7 | 21.3
18 | 22.5 | 16.2 | 20
19 | 21 | 15.4 | 18.9
20 | 18.9 | 14.4 | 16.6
21 | 18 | 13.5 | 14.8
22 | 16.4 | 12.9 | 13.3
23 | 16.2 | 12.4 | 13.9
0 | 16 | 13.6 | 14.5
1 | 13.4 | 13.4 | 14
2 | 11.5 | 13.3 | 13.7
3 | 11.3 | 13.2 | 13.5
4 | 11.2 | 13 | 13.3
5 | 11.2 | 12.9 | 13.4
6 | 11.8 | 13.3 | 13.4
7 | 12.6 | 13.8 | 14
8 | 14.7 | 14.4 | 16.3
9 | 16 | 15 | 17.5
10 | 17.8 | 15.4 | 18.3
11 | 18.8 | 15.8 | 18.7
12 | 19.7 | 16.2 | 19.8
13 | 20.3 | 16.4 | 20.4
14 | 20.8 | 16.5 | 20.6
15 | 20.1 | 16.6 | 20.7
16 | 20.8 | 16.5 | 20.2
17 | 20.3 | 16.2 | 20.4
18 | 19.4 | 15.9 | 19.5
19 | 17.7 | 15.5 | 18.3
20 | 16 | 14.9 | 17.8
21 | 15 | 14.4 | 16
22 | 13.5 | 14 | 16
23 | 13.9 | 13.8 | 15.7
0 | 14.4 | 14.9 | 15.4
1 | 13 | 14.7 | 13.7
2 | 11.9 | 14.6 | 12.5
3 | 11.6 | 14.4 | 12.1
4 | 11.2 | 14.2 | 12
5 | 11.2 | 14.1 | 11.9
6 | 11.3 | 14.5 | 12.6
7 | 13.4 | 15.2 | 13.4
8 | 15.2 | 16 | 16.3
9 | 16.7 | 16.7 | 17.7
10 | 18.7 | 17.3 | 19.4
11 | 19.9 | 17.8 | 21.7
12 | 21 | 18.2 | 22.2
13 | 21.4 | 18.5 | 22.5
14 | 21.4 | 18.7 | 22.3
15 | 22 | 18.7 | 22.9
16 | 22 | 18.6 | 23.3
17 | 21.2 | 18.3 | 22.9
18 | 20.2 | 17.9 | 21.6
19 | 18.9 | 17.3 | 19.7
20 | 16.9 | 16.6 | 18.4
21 | 15.1 | 15.9 | 16.3
22 | 14.6 | 15.5 | 15.2
23 | 15.8 | 15.2 | 15.8
0 | 17 | 16.6 | 16.5
1 | 17.2 | 16.5 | 16.1
2 | 17.3 | 16.4 | 15.5
3 | 17.2 | 16.3 | 15.5
4 | 17 | 16.2 | 15.4
5 | 17.1 | 16.2 | 15.5
6 | 17.2 | 16.4 | 15.6
7 | 18 | 16.7 | 17.2
8 | 18.6 | 17.1 | 18.5
9 | 19.5 | 17.5 | 20.5
10 | 20.4 | 17.8 | 22.3
11 | 21.4 | 18.1 | 23.2
12 | 21.8 | 18.3 | 23.9
13 | 22 | 18.4 | 25
14 | 22.1 | 18.5 | 25.3
15 | 22.1 | 18.5 | 25.1
16 | 22 | 18.5 | 25.2
17 | 21.6 | 18.3 | 24.8
18 | 21.3 | 18.1 | 24.1
19 | 20.1 | 17.8 | 22.7
20 | 19.8 | 17.5 | 21.2
21 | 19.2 | 17.1 | 19.8
22 | 18.4 | 16.9 | 18.1
23 | 18.2 | 16.7 | 17.8
0 | 18.1 | 13.5 | 17.4
1 | 16.1 | 13.2 | 14.8
2 | 14.7 | 12.9 | 12.9
3 | 14 | 12.6 | 12.3
4 | 14 | 12.3 | 12.1
5 | 14.1 | 12.1 | 12
6 | 14.9 | 12.8 | 13.2
7 | 15.9 | 14.1 | 14.5
8 | 17.5 | 15.6 | 17.4
9 | 18.8 | 16.8 | 20
10 | 20.2 | 17.9 | 21.9
11 | 21.5 | 18.9 | 23.1
12 | 22.4 | 19.7 | 24.9
13 | 22.9 | 20.2 | 25.3
14 | 23.3 | 20.5 | 26.2
15 | 22.6 | 20.5 | 26.7
16 | 22.9 | 20.3 | 26.6
17 | 22.6 | 19.8 | 25.3
18 | 21.2 | 19.1 | 23.9
19 | 20.1 | 18 | 22.6
20 | 19 | 16.7 | 20.2
21 | 17.3 | 15.5 | 17.7
22 | 16.5 | 14.6 | 16.6
23 | 16.3 | 14 | 16.5
0 | 16.2 | 14.2 | 16.3
1 | 13.8 | 13.7 | 15.1
2 | 12.1 | 13.4 | 13.9
3 | 12 | 13 | 13.7
4 | 12 | 12.6 | 13.6
5 | 12 | 12.4 | 13.5
6 | 12.5 | 13.3 | 14.4
7 | 13.1 | 14.9 | 15.3
8 | 15 | 16.7 | 18.2
9 | 16.7 | 18.3 | 20
10 | 17.7 | 19.6 | 21.8
11 | 19.1 | 20.8 | 23
12 | 19.5 | 21.8 | 25.5
13 | 20.1 | 22.5 | 26
14 | 20.3 | 22.8 | 25.3
15 | 20.8 | 22.9 | 26
16 | 20.8 | 22.6 | 25.6
17 | 20.7 | 22 | 25.9
18 | 19.1 | 21.1 | 23.9
19 | 18.2 | 19.7 | 22.5
20 | 17.3 | 18.1 | 20.5
21 | 15.5 | 16.6 | 18.3
22 | 14.1 | 15.6 | 17.1
23 | 14.7 | 14.8 | 17.3
0 | 15.3 | 15.2 | 17.5
1 | 15.1 | 15.1 | 16.6
2 | 14.8 | 14.8 | 16.2
3 | 15.1 | 14.6 | 15.4
4 | 14.9 | 14.4 | 15.2
5 | 14.8 | 14 | 14.9
6 | 14.6 | 14.5 | 15.5
7 | 15.3 | 15.4 | 16.2
8 | 16 | 16.8 | 18.4
9 | 18.1 | 18.1 | 20.2
10 | 19.5 | 19.1 | 22.3
11 | 19.2 | 20 | 23.3
12 | 20.3 | 20.7 | 24.6
13 | 20.3 | 21.2 | 25.7
14 | 20.4 | 21.1 | 25.7
15 | 20.6 | 21.4 | 25.4
16 | 20.1 | 21.3 | 25.6
17 | 20.2 | 20.8 | 24.6
18 | 19.9 | 20 | 24.7
19 | 18.1 | 18.9 | 22.3
20 | 17.1 | 17.7 | 20.5
21 | 17 | 16.8 | 19.2
22 | 16 | 16.2 | 18.4
23 | 16.8 | 15.6 | 17.4
0 | 17.6 | 14.4 | 16.4
1 | 16.1 | 14.2 | 13.3
2 | 14.8 | 14 | 11.3
3 | 14.8 | 13.8 | 11.2
4 | 14.8 | 13.6 | 11
5 | 14.9 | 13.2 | 11
6 | 14.9 | 13.7 | 11.3
7 | 15.5 | 14.6 | 11.8
8 | 18.1 | 16 | 13.6
9 | 20.2 | 17.3 | 15.7
10 | 21.7 | 18.3 | 17.1
11 | 22.1 | 19.2 | 18.4
12 | 22.6 | 19.9 | 20.5
13 | 22.1 | 20.4 | 20.6
14 | 23.3 | 20.1 | 20.6
15 | 22.7 | 20.6 | 20
16 | 23 | 20.5 | 20.1
17 | 22.7 | 20.1 | 19.1
18 | 22.1 | 19.2 | 18.9
19 | 19.8 | 18.1 | 18.3
20 | 18.4 | 16.9 | 16.5
21 | 17.7 | 16 | 14.3
22 | 17.8 | 15.4 | 13.4
23 | 17.4 | 14.8 | 14.3
0 | 17.1 | 15.5 | 15.2
1 | 15 | 15.4 | 14.2
2 | 13.4 | 15.3 | 13.5
3 | 13.3 | 15.2 | 13.5
4 | 12.9 | 15.1 | 13.4
5 | 12.9 | 15 | 13.4
6 | 12.9 | 15.2 | 13.6
7 | 14.6 | 15.6 | 13.8
8 | 16.4 | 16.1 | 14.7
9 | 19.6 | 16.6 | 16.4
10 | 21.4 | 17.1 | 17.1
11 | 22.2 | 17.4 | 18.4
12 | 23 | 17.7 | 18.6
13 | 23.9 | 17.9 | 18.6
14 | 24.4 | 17.5 | 18.7
15 | 23.8 | 18 | 19.1
16 | 24.1 | 17.9 | 18.7
17 | 23.8 | 17.7 | 18.6
18 | 23.2 | 17.4 | 18.1
19 | 20.1 | 17 | 17.3
20 | 18.6 | 16.5 | 16.8
21 | 17.5 | 16.1 | 15.6
22 | 16 | 15.9 | 14.4
23 | 17.1 | 15.6 | 14.5
0 | 18.1 | 15.2 | 14.7
1 | 17.7 | 15.1 | 12.5
2 | 17.3 | 14.9 | 10.9
3 | 17.6 | 14.8 | 10.7
4 | 17.4 | 14.7 | 10.5
5 | 17.2 | 14.4 | 10.3
6 | 17.5 | 14.7 | 11
7 | 17.8 | 15.4 | 11.7
8 | 19.1 | 16.3 | 13.9
9 | 21.9 | 17.1 | 16.3
10 | 23.5 | 17.9 | 19.1
11 | 25.1 | 18.4 | 21
12 | 25.3 | 18.9 | 21.4
13 | 25.5 | 19.3 | 22.1
14 | 25.7 | 19.2 | 22.4
15 | 25.3 | 19.4 | 21.8
16 | 25.3 | 19.3 | 21.9
17 | 25.7 | 19 | 21.7
18 | 24.5 | 18.4 | 20
19 | 23.4 | 17.7 | 18.3
20 | 21.9 | 16.9 | 16.9
21 | 19.8 | 16.3 | 15.4
22 | 19.5 | 15.9 | 14.3
23 | 19.8 | 15.5 | 14.5
0 | 20 | 15.4 | 14.7
1 | 17.9 | 15.2 | 14.4
2 | 16.5 | 15 | 13.7
3 | 16.3 | 14.8 | 14.4
4 | 16.1 | 14.6 | 13.2
5 | 16 | 14.2 | 13.1
6 | 16.2 | 14.7 | 12.9
7 | 16.3 | 15.6 | 14.7
8 | 19.2 | 16.9 | 16.5
9 | 20 | 18.2 | 18.8
10 | 21.1 | 19.2 | 21.4
11 | 23.7 | 20 | 22.6
12 | 23.8 | 20.7 | 24.1
13 | 24.1 | 21.2 | 24.5
14 | 24.5 | 20.8 | 24.8
15 | 24.1 | 21.4 | 24.9
16 | 23.9 | 21.3 | 24.5
17 | 23.7 | 20.8 | 24.5
18 | 22 | 20 | 23.2
19 | 22 | 18.9 | 20.7
20 | 20 | 17.8 | 18.4
21 | 18.9 | 16.9 | 18.2
22 | 18.2 | 16.3 | 15.8
23 | 19.3 | 15.7 | 15.3
0 | 20.5 | 14.2 | 14.7
1 | 18.9 | 14.1 | 11.4
2 | 17.6 | 13.8 | 9.2
3 | 17.4 | 13.5 | 8.6
4 | 17.3 | 13.3 | 8.3
5 | 17.2 | 12.9 | 8.3
6 | 18 | 13.4 | 8.3
7 | 18.7 | 14.5 | 9.6
8 | 19.2 | 16 | 12.1
9 | 21.9 | 17.5 | 15.1
10 | 24.1 | 18.7 | 17.1
11 | 24.9 | 19.6 | 17.8
12 | 25.8 | 20.4 | 19.9
13 | 26.1 | 21 | 20.7
14 | 25.5 | 21.1 | 21.2
15 | 25.6 | 21.2 | 20.6
16 | 25.6 | 21.1 | 20.2
17 | 25.6 | 20.6 | 20.7
18 | 25 | 19.7 | 19.1
19 | 22.6 | 18.4 | 17.7
20 | 21.5 | 17 | 15
21 | 19.8 | 16 | 12.9
22 | 19.3 | 15.3 | 12.1
23 | 20.2 | 14.6 | 12.9
0 | 21.2 | 15.9 | 13.7
1 | 19.8 | 15.8 | 13.4
2 | 18.6 | 15.6 | 12.9
3 | 18.7 | 15.4 | 12.8
4 | 18.8 | 15.2 | 12.7
5 | 18.9 | 14.8 | 12.4
6 | 19.1 | 15.3 | 12.9
7 | 19.4 | 16.1 | 13.3
8 | 19.7 | 17.3 | 15.3
9 | 21.1 | 18.5 | 18
10 | 22 | 19.5 | 19.2
11 | 22.8 | 20.3 | 19.7
12 | 23.2 | 20.9 | 20.6
13 | 23.1 | 21.4 | 21.3
14 | 22.8 | 21.4 | 21.6
15 | 23.4 | 21.5 | 21.8
16 | 23.1 | 21.5 | 21.4
17 | 22.7 | 21.1 | 21.7
18 | 22.4 | 20.3 | 19.9
19 | 22.2 | 19.3 | 19.8
20 | 20.1 | 18.2 | 17
21 | 20.2 | 17.3 | 15.5
22 | 19.6 | 16.8 | 16.1
23 | 19.6 | 16.3 | 15.6
0 | 19.7 | 18.6 | 15.2
1 | 17.1 | 18.5 | 13.6
2 | 15.6 | 18.3 | 12.4
3 | 15.6 | 18.2 | 12.5
4 | 15.4 | 18 | 12.2
5 | 15.3 | 17.8 | 12
6 | 16.3 | 18.1 | 12.7
7 | 17.3 | 18.8 | 13.5
8 | 18.7 | 19.7 | 16.1
9 | 20.1 | 20.6 | 17.7
10 | 23 | 21.3 | 19.9
11 | 22.2 | 21.9 | 21.5
12 | 24.1 | 22.4 | 22.3
13 | 24.1 | 22.8 | 23.5
14 | 23.7 | 22.6 | 23.4
15 | 24.7 | 22.9 | 23.7
16 | 24.3 | 22.9 | 23.3
17 | 24.3 | 22.5 | 23
18 | 23.1 | 22 | 22.1
19 | 21.9 | 21.2 | 19.7
20 | 19.2 | 20.3 | 18.6
21 | 19.1 | 19.7 | 16.9
22 | 17.3 | 19.3 | 15.5
23 | 18.1 | 18.9 | 15.4
0 | 18.9 | 17.3 | 15.4
1 | 18.1 | 17 | 13.3
2 | 17.2 | 16.7 | 11.6
3 | 17.2 | 16.4 | 11.4
4 | 17.4 | 16.1 | 11.3
5 | 17.2 | 15.5 | 11.3
6 | 17 | 16.3 | 11.3
7 | 17.7 | 17.6 | 12.7
8 | 18.5 | 19.5 | 14.6
9 | 20.6 | 21.4 | 15.5
10 | 22.5 | 22.9 | 17
11 | 22.9 | 24.1 | 17.9
12 | 23.9 | 25.2 | 19.5
13 | 23.4 | 26 | 19.7
14 | 23.5 | 26.1 | 19.7
15 | 23.9 | 26.2 | 19.9
16 | 23.5 | 26.1 | 19.4
17 | 23.4 | 25.4 | 19.6
18 | 22.5 | 24.2 | 18.1
19 | 20.7 | 22.6 | 16.9
20 | 19.9 | 20.9 | 15.7
21 | 18.7 | 19.5 | 14.8
22 | 18.8 | 18.7 | 13.3
23 | 19.2 | 17.8 | 13.8
0 | 19.5 | 13.2 | 14.2
1 | 16.8 | 13 | 12.8
2 | 15.1 | 12.4 | 11.9
3 | 14.9 | 11.9 | 11.1
4 | 14.7 | 11.4 | 11.2
5 | 14.6 | 10.5 | 11.3
6 | 15.2 | 11.7 | 11.3
7 | 15.9 | 13.8 | 11.4
8 | 17.2 | 16.9 | 14.4
9 | 19.7 | 19.9 | 15.7
10 | 19.2 | 22.3 | 18.4
11 | 21.8 | 24.3 | 17.8
12 | 22.4 | 25.9 | 19.7
13 | 22.3 | 27.2 | 19.9
14 | 22.5 | 26.9 | 20.4
15 | 22.6 | 27.4 | 20.2
16 | 22.9 | 27.3 | 20
17 | 21.9 | 26.3 | 20.4
18 | 20.6 | 24.4 | 18.9
19 | 19.4 | 21.8 | 18
20 | 18.7 | 19 | 15.5
21 | 17.7 | 16.9 | 14.4
22 | 17.3 | 15.5 | 13.7
23 | 17 | 14.1 | 13.8
0 | 16.8 | 16.9 | 13.9
1 | 14.8 | 16.7 | 12
2 | 13.9 | 16.4 | 10.8
3 | 12.9 | 16.2 | 10.4
4 | 13.2 | 15.9 | 10.2
5 | 13.5 | 15.5 | 10.3
6 | 13.1 | 16.1 | 10.5
7 | 14.1 | 17.1 | 11.3
8 | 15.3 | 18.7 | 13
9 | 18.1 | 20.2 | 14.8
10 | 18.6 | 21.4 | 16.1
11 | 20.5 | 22.4 | 18.1
12 | 21 | 23.2 | 18.6
13 | 21.4 | 23.8 | 18.5
14 | 21.5 | 23.6 | 19.1
15 | 21.8 | 24 | 18.8
16 | 21.4 | 23.9 | 18.5
17 | 21.6 | 23.4 | 18.2
18 | 19.9 | 22.4 | 18
19 | 19.3 | 21.1 | 16.2
20 | 17.1 | 19.7 | 14.9
21 | 15.7 | 18.7 | 13.6
22 | 15.2 | 18 | 12.7
23 | 15.3 | 17.3 | 13.5
0 | 15.5 | 14.8 | 14.2
1 | 13.5 | 14.6 | 13.7
2 | 12.4 | 14.1 | 13.4
3 | 12.2 | 13.8 | 13.2
4 | 11.9 | 13.4 | 13.2
5 | 12.1 | 12.8 | 13.2
6 | 12.2 | 13.7 | 13.1
7 | 13.2 | 15.2 | 13.9
8 | 14.8 | 17.3 | 14.6
9 | 18 | 19.5 | 15.2
10 | 18.6 | 21.2 | 15.4
11 | 19.8 | 22.6 | 16.4
12 | 21.6 | 23.7 | 16.8
13 | 21.3 | 24.6 | 16.3
14 | 22 | 24.5 | 16.2
15 | 22 | 24.8 | 16.8
16 | 21.5 | 24.7 | 16.5
17 | 21.6 | 24 | 16.6
18 | 19.9 | 22.6 | 15.9
19 | 19.6 | 20.8 | 15.8
20 | 16.7 | 18.9 | 14.1
21 | 15.9 | 17.3 | 14.6
22 | 14 | 16.4 | 14.2
23 | 14.8 | 15.4 | 14.1
0 | 15.6 | 12.5 | 14.1
1 | 13.9 | 12.4 | 12.6
2 | 12.6 | 12.1 | 11.6
3 | 12.6 | 11.9 | 11.3
4 | 12.5 | 11.7 | 11
5 | 12.6 | 11.3 | 11.2
6 | 12.6 | 11.8 | 11.4
7 | 13.3 | 12.8 | 11.9
8 | 15.4 | 14.1 | 13.8
9 | 17 | 15.5 | 15.3
10 | 18.8 | 16.5 | 17.2
11 | 19.7 | 17.4 | 17.6
12 | 21 | 18.1 | 18.7
13 | 20.9 | 18.7 | 19.2
14 | 20.7 | 18.6 | 19.2
15 | 20.6 | 18.8 | 19.4
16 | 21.2 | 18.7 | 19.5
17 | 21 | 18.3 | 19.5
18 | 20.7 | 17.4 | 17.1
19 | 17.5 | 16.3 | 17
20 | 16.1 | 15.1 | 15.5
21 | 14.9 | 14.1 | 13.8
22 | 15 | 13.5 | 13.4
23 | 16.5 | 12.9 | 13.9
0 | 17.9 | 13.8 | 14.4
1 | 17.8 | 13.8 | 13.4
2 | 18 | 13.7 | 12.4
3 | 17.5 | 13.7 | 12.2
4 | 17.3 | 13.7 | 12.1
5 | 17 | 13.6 | 12.2
6 | 17.3 | 13.7 | 12.3
7 | 17.5 | 13.8 | 12.8
8 | 19.6 | 14 | 15.3
9 | 21.7 | 14.2 | 16.6
10 | 22.6 | 14.4 | 18.2
11 | 24.8 | 14.5 | 18.8
12 | 24.9 | 14.6 | 19.2
13 | 25.2 | 14.7 | 20.3
14 | 25 | 14.5 | 19.9
15 | 25.7 | 14.7 | 19.8
16 | 25.4 | 14.7 | 19.7
17 | 24.9 | 14.6 | 19.5
18 | 25.6 | 14.5 | 18.8
19 | 23.1 | 14.3 | 17.9
20 | 21.9 | 14.2 | 16.2
21 | 20.3 | 14 | 14.8
22 | 18.6 | 13.9 | 13.9
23 | 19.6 | 13.8 | 14.3
0 | 20.6 | 12.4 | 14.6
1 | 19.3 | 12.2 | 12.2
2 | 18.4 | 11.9 | 10.6
3 | 17.2 | 11.7 | 10.2
4 | 16.9 | 11.4 | 10.2
5 | 16.7 | 11 | 10.2
6 | 17.1 | 11.6 | 10.7
7 | 17.6 | 12.7 | 11.3
8 | 20.6 | 14.3 | 12.8
9 | 23.7 | 15.8 | 14.3
10 | 26.1 | 17 | 15.5
11 | 27.3 | 18 | 15.7
12 | 30.2 | 18.9 | 17.5
13 | 29.9 | 19.5 | 17.7
14 | 30.1 | 19.4 | 18.1
15 | 30.3 | 19.6 | 17.5
16 | 30.1 | 19.6 | 17.7
17 | 30.1 | 19 | 17.9
18 | 28 | 18.1 | 17.8
19 | 25.7 | 16.7 | 15.7
20 | 23.5 | 15.3 | 13.2
21 | 22 | 14.2 | 12.4
22 | 21.2 | 13.5 | 12.5
23 | 20.4 | 12.8 | 12.7
0 | 19.6 | 14.9 | 12.9
1 | 16.9 | 14.8 | 11.3
2 | 14.9 | 14.6 | 9.7
3 | 14.8 | 14.4 | 9.9
4 | 14.3 | 14.3 | 10.1
5 | 14 | 14 | 9.9
6 | 14.6 | 14.4 | 10.2
7 | 15.5 | 15 | 10.6
8 | 17.7 | 16 | 12.1
9 | 20.5 | 16.9 | 13.4
10 | 21.8 | 17.7 | 15.1
11 | 23.7 | 18.3 | 16.2
12 | 25.4 | 18.8 | 17
13 | 25.2 | 19.2 | 17.3
14 | 24.7 | 18.7 | 17.4
15 | 25.8 | 19.3 | 17.6
16 | 25.4 | 19.3 | 17.2
17 | 24.8 | 18.9 | 17.3
18 | 23.3 | 18.3 | 15.7
19 | 21.7 | 17.5 | 14.9
20 | 19.7 | 16.7 | 13.3
21 | 17.7 | 16 | 12.7
22 | 16.9 | 15.6 | 11.4
23 | 16.6 | 13.2 | 12.8
0 | 16.4 | 10.7 | 14.2
1 | 16.1 | 8.2 | 15.6
2 | 15.9 | 5.8 | 17
3 | 15.2 | 5.5 | 17
4 | 15 | 5.1 | 16.8
5 | 14.9 | 4 | 16.5
6 | 14.9 | 4.8 | 17
7 | 16.4 | 6 | 17.3
8 | 18 | 8.4 | 18.6
9 | 20.1 | 11.1 | 20.8
10 | 22.4 | 13.2 | 21.7
11 | 23.8 | 14.8 | 23
12 | 23.7 | 16.1 | 23.5
13 | 24.6 | 16.7 | 23.9
14 | 24.3 | 16.8 | 24
15 | 24.7 | 16.6 | 23.6
16 | 24.2 | 16.7 | 23.7
17 | 24.3 | 15.6 | 23.9
18 | 23.5 | 13.8 | 23
19 | 21.4 | 11.7 | 22
20 | 19.5 | 9.9 | 19.7
21 | 18.3 | 8.7 | 19.4
22 | 17.6 | 7.9 | 18.8
23 | 17.8 | 6.6 | 18.8
0 | 18 | 11 | 18.7
1 | 17 | 11.1 | 16.6
2 | 16.2 | 10.8 | 15
3 | 16 | 10.6 | 14.9
4 | 15.9 | 10.4 | 14.9
5 | 16.1 | 9.8 | 14.8
6 | 16.3 | 10.2 | 14.7
7 | 16 | 10.9 | 15.4
8 | 17.8 | 12.3 | 16.1
9 | 20.2 | 13.8 | 18.6
10 | 22.4 | 15 | 19.8
11 | 24 | 15.9 | 21
12 | 24.1 | 16.7 | 21.9
13 | 24.3 | 17 | 22
14 | 24.5 | 17.1 | 21.7
15 | 24.5 | 17 | 21.3
16 | 24.3 | 17 | 21.5
17 | 24.4 | 16.4 | 21.5
18 | 23.2 | 15.4 | 21
19 | 21.7 | 14.1 | 19.5
20 | 20.6 | 13.1 | 18.4
21 | 19.1 | 12.5 | 17.2
22 | 18.3 | 12 | 17.5
23 | 18 | 11.3 | 17
0 | 17.7 | 13.2 | 16.5
1 | 16 | 13.3 | 14.7
2 | 15.1 | 13 | 13.2
3 | 15 | 12.7 | 12.7
4 | 15 | 12.4 | 12.4
5 | 15 | 11.5 | 12.2
6 | 15 | 12.1 | 12.7
7 | 15.9 | 13.1 | 13.3
8 | 17 | 15.1 | 15.1
9 | 17.9 | 17.2 | 17.6
10 | 19.4 | 19 | 19.9
11 | 20.2 | 20.3 | 20.9
12 | 20.4 | 21.3 | 22.4
13 | 20.6 | 21.6 | 22.7
14 | 20.5 | 21.9 | 22.1
15 | 20.8 | 21.8 | 22.1
16 | 20.4 | 21.8 | 22.3
17 | 20.2 | 20.9 | 21.6
18 | 19.5 | 19.4 | 21
19 | 18.6 | 17.7 | 19.3
20 | 18 | 16.3 | 17
21 | 17.6 | 15.3 | 16.3
22 | 16.5 | 14.6 | 14.7
23 | 16.4 | 13.6 | 14.3
0 | 16.2 | 16.5 | 13.9
1 | 13.8 | 16.6 | 10.7
2 | 11.8 | 16.3 | 8.7
3 | 11.8 | 16.1 | 8.1
4 | 11.8 | 15.9 | 7.7
5 | 12.2 | 15.3 | 7.7
6 | 12.2 | 15.8 | 8
7 | 12.4 | 16.4 | 8.3
8 | 12.7 | 17.7 | 11.7
9 | 13.7 | 19.2 | 13.5
10 | 14.9 | 20.4 | 16.4
11 | 15.8 | 21.3 | 17.5
12 | 16.1 | 22 | 18.8
13 | 15.8 | 22.1 | 19
14 | 16 | 22.4 | 18.9
15 | 16.1 | 22.1 | 19.4
16 | 15.8 | 22.3 | 19
17 | 16.4 | 21.7 | 17.7
18 | 15.1 | 20.7 | 16.8
19 | 14.9 | 19.5 | 15.7
20 | 13.6 | 18.6 | 13.6
21 | 13.1 | 17.9 | 12.1
22 | 12.5 | 17.5 | 11.6
23 | 13.1 | 16.8 | 11.3
0 | 13.7 | 16 | 11
1 | 12.3 | 16.1 | 10.5
2 | 11 | 15.9 | 10.1
3 | 10.9 | 15.6 | 10.4
4 | 11.4 | 15.4 | 10.3
5 | 11.1 | 14.6 | 10.2
6 | 10.8 | 15.1 | 10.1
7 | 12 | 16 | 11.1
8 | 13.2 | 17.6 | 12.2
9 | 15.4 | 19.4 | 13.8
10 | 16.8 | 20.8 | 15.5
11 | 17.5 | 21.9 | 16.2
12 | 18.3 | 22.8 | 16
13 | 18.3 | 23.2 | 16.4
14 | 18.7 | 23.3 | 16.5
15 | 18.5 | 22.8 | 16.4
16 | 18.2 | 23.2 | 16.4
17 | 18.3 | 22.5 | 16.2
18 | 17.1 | 21.2 | 15.5
19 | 15.4 | 19.8 | 14.4
20 | 13.9 | 18.6 | 12.9
21 | 13.9 | 17.8 | 11.5
22 | 13.1 | 17.2 | 12
23 | 15.3 | 16.4 | 12.3
0 | 17.5 | 13.2 | 12.7
1 | 17.7 | 13.5 | 11.9
2 | 17.8 | 13 | 11.1
3 | 17.7 | 12.6 | 11.1
4 | 17.5 | 12.2 | 10.7
5 | 17.7 | 10.9 | 10.4
6 | 17.8 | 11.8 | 10.8
7 | 18.7 | 13.2 | 11.3
8 | 19 | 15.8 | 13.7
9 | 20.9 | 18.8 | 16.1
10 | 22.5 | 21.1 | 17.3
11 | 22.8 | 22.9 | 19.1
12 | 23.4 | 24.3 | 20.5
13 | 23.5 | 24.9 | 20.4
14 | 23.7 | 25.1 | 20.7
15 | 23.4 | 25 | 20.1
16 | 23.5 | 25 | 20.2
17 | 23.6 | 23.8 | 19.6
18 | 22.5 | 21.7 | 19.1
19 | 21.6 | 19.4 | 16.8
20 | 21 | 17.5 | 15.9
21 | 19.5 | 16.2 | 14.7
22 | 19.6 | 15.2 | 13.4
23 | 18.9 | 13.8 | 13.8
0 | 18.2 | 16.2 | 14.2
1 | 15.7 | 16.4 | 13.7
2 | 14 | 16 | 12.8
3 | 13.8 | 15.7 | 11.7
4 | 13.5 | 15.3 | 11.9
5 | 13.3 | 14.3 | 11.9
6 | 13.8 | 15 | 12.3
7 | 14.5 | 16.1 | 13
8 | 16.3 | 18.3 | 15.4
9 | 18.9 | 20.7 | 19.2
10 | 20.6 | 22.6 | 21.1
11 | 21.8 | 24.1 | 23.1
12 | 23 | 25.3 | 24.8
13 | 23.2 | 25.8 | 24.8
14 | 23.2 | 25.9 | 24.8
15 | 23.5 | 25.7 | 24.9
16 | 23.1 | 25.8 | 24.8
17 | 22.8 | 24.8 | 24.3
18 | 21.4 | 23.1 | 22.9
19 | 19.4 | 21.2 | 20.1
20 | 18.2 | 19.6 | 18.2
21 | 17.4 | 18.6 | 17.1
22 | 15.8 | 17.8 | 15.3
23 | 16.5 | 16.6 | 15.8
0 | 17.1 | 13.9 | 16.3
1 | 16.2 | 14.1 | 15.8
2 | 15.3 | 13.8 | 15.8
3 | 15.1 | 13.5 | 14.2
4 | 15 | 13.2 | 14.1
5 | 14.9 | 12.3 | 14
6 | 15.2 | 12.9 | 14.2
7 | 15.5 | 13.9 | 14.5
8 | 16.8 | 15.7 | 15.7
9 | 18.9 | 17.8 | 18.4
10 | 20.5 | 19.5 | 19.4
11 | 21.2 | 20.7 | 21
12 | 21.8 | 21.8 | 22
13 | 22 | 22 | 21.6
14 | 21.7 | 22.3 | 22
15 | 21.7 | 22 | 21.5
16 | 22.1 | 22.2 | 21.8
17 | 21.6 | 21.4 | 21.9
18 | 19.7 | 19.9 | 19.9
19 | 19.6 | 18.3 | 19.3
20 | 17.8 | 16.9 | 17.1
21 | 17.7 | 16 | 16.4
22 | 17.3 | 15.3 | 15.8
23 | 17.5 | 14.3 | 15.6
0 | 17.6 | 15.8 | 15.4
1 | 16.7 | 15.9 | 12.4
2 | 16.1 | 15.7 | 10.4
3 | 15.9 | 15.6 | 9.4
4 | 16.1 | 15.5 | 9.1
5 | 16 | 15.1 | 9
6 | 15.9 | 15.4 | 9.6
7 | 16.4 | 15.8 | 10.3
8 | 17 | 16.6 | 14.3
9 | 18.5 | 17.4 | 17.5
10 | 19.5 | 18.1 | 20.2
11 | 20.6 | 18.7 | 21.9
12 | 20.4 | 19.1 | 23.9
13 | 20.8 | 18.9 | 24.6
14 | 20.7 | 19.3 | 24.7
15 | 20.8 | 19 | 24.6
16 | 21 | 19.3 | 24.2
17 | 20.4 | 18.9 | 23.7
18 | 20.4 | 18.3 | 21.7
19 | 19 | 17.6 | 18.5
20 | 18.6 | 17.1 | 16.9
21 | 18.1 | 16.7 | 14.9
22 | 17.7 | 16.4 | 13.6
23 | 18.1 | 16 | 13
0 | 18.5 | 11.8 | 12.4
1 | 17.8 | 11.9 | 10
2 | 17.3 | 11.7 | 8.2
3 | 17.6 | 11.6 | 7.9
4 | 17.6 | 11.4 | 7.6
5 | 17.3 | 10.9 | 7.3
6 | 17 | 11.3 | 7.8
7 | 18 | 11.8 | 8.2
8 | 18.9 | 12.8 | 11.3
9 | 21.1 | 14 | 14.7
10 | 22.2 | 14.9 | 17.6
11 | 22.1 | 15.6 | 20
12 | 23.6 | 16.1 | 21.7
13 | 23.2 | 15.9 | 21.6
14 | 23.6 | 16.4 | 21.7
15 | 23.3 | 16.2 | 21.9
16 | 23.5 | 16.4 | 21.5
17 | 23.1 | 15.9 | 20.9
18 | 22.3 | 15.1 | 18.4
19 | 20.8 | 14.2 | 17.3
20 | 19.7 | 13.5 | 14.9
21 | 19.7 | 12.9 | 12.6
22 | 18.2 | 12.6 | 11.5
23 | 18.6 | 12 | 11.4
0 | 18.9 | 11.9 | 11.3
1 | 17.5 | 12.1 | 10.1
2 | 16.6 | 11.8 | 9.1
3 | 16.2 | 11.5 | 9.3
4 | 16.1 | 11.3 | 9.1
5 | 16.2 | 10.5 | 8.7
6 | 16.2 | 11 | 8.4
7 | 16.5 | 11.9 | 10.2
8 | 16.7 | 13.5 | 12
9 | 17.2 | 15.4 | 14
10 | 17.7 | 16.8 | 17.3
11 | 18 | 17.9 | 18.4
12 | 17.9 | 18.8 | 20
13 | 17.7 | 18.9 | 19.7
14 | 17.7 | 19.3 | 19.5
15 | 18.2 | 19.1 | 19.9
16 | 17.8 | 19.2 | 20.1
17 | 17.8 | 18.5 | 19.3
18 | 17.2 | 17.2 | 17.9
19 | 16.8 | 15.8 | 15.1
20 | 17.4 | 14.6 | 14.4
21 | 17.7 | 13.7 | 12.9
22 | 16.1 | 13.2 | 12.3
23 | 16.4 | 12.3 | 11.9
0 | 16.6 | 13 | 11.4
1 | 15.3 | 13.2 | 10
2 | 14.4 | 12.8 | 8.8
3 | 13.9 | 12.5 | 8.6
4 | 14.1 | 12.1 | 8.3
5 | 14 | 11 | 8
6 | 13.9 | 11.8 | 8.5
7 | 14.8 | 13 | 9
8 | 15.7 | 15.3 | 11.3
9 | 17.7 | 17.8 | 13.6
10 | 19.5 | 19.9 | 15.3
11 | 20.8 | 21.4 | 17.8
12 | 21.3 | 22.7 | 18.8
13 | 21 | 23 | 18.8
14 | 21.3 | 23.3 | 18.7
15 | 21.4 | 23.1 | 19
16 | 21.1 | 23.2 | 18.8
17 | 20.7 | 22.2 | 18.3
18 | 20.3 | 20.4 | 16.8
19 | 18.1 | 18.4 | 14.4
20 | 16.9 | 16.7 | 13.2
21 | 16.5 | 15.6 | 12.4
22 | 16 | 14.8 | 10.9
23 | 15.4 | 13.5 | 10.9
0 | 14.8 | 11.4 | 10.9
1 | 11.6 | 11.6 | 9.4
2 | 8.9 | 11.1 | 8.2
3 | 9.2 | 10.6 | 8
4 | 8.6 | 10.2 | 7.3
5 | 8.6 | 8.8 | 6.6
6 | 8.6 | 9.8 | 7.1
7 | 9.8 | 11.3 | 7.6
8 | 11.1 | 14.3 | 11.4
9 | 14.2 | 17.6 | 14.8
10 | 16.2 | 20.3 | 18.2
11 | 17.8 | 22.3 | 19.5
12 | 19.5 | 23.9 | 21.5
13 | 19.1 | 24.5 | 22.1
14 | 19.6 | 24.8 | 22.5
15 | 19.1 | 24.6 | 22.3
16 | 19.1 | 24.7 | 22.4
17 | 18.8 | 23.3 | 21.8
18 | 17.1 | 21 | 19.7
19 | 15.5 | 18.3 | 16.6
20 | 13.6 | 16.2 | 14.3
21 | 12.9 | 14.7 | 13.4
22 | 12.1 | 13.6 | 11.3
23 | 13 | 12 | 11.4
0 | 13.9 | 12.6 | 11.5
1 | 14.4 | 12.8 | 11
2 | 14.5 | 12.5 | 10.5
3 | 14.4 | 12.2 | 10.1
4 | 14.4 | 11.9 | 9.4
5 | 14.2 | 10.9 | 9.2
6 | 13.9 | 11.6 | 9
7 | 15.1 | 12.6 | 10.9
8 | 16.3 | 14.6 | 12.9
9 | 17.5 | 16.8 | 16
10 | 19.7 | 18.5 | 18.4
11 | 20.2 | 19.8 | 20.1
12 | 20.7 | 20.9 | 21.2
13 | 20.8 | 21 | 22.3
14 | 21.1 | 21.5 | 22.1
15 | 20.5 | 21.3 | 22.5
16 | 20.7 | 21.4 | 22.1
17 | 21.1 | 20.5 | 22.3
18 | 19.6 | 19 | 19.8
19 | 18.6 | 17.2 | 18.1
20 | 16.9 | 15.8 | 15.2
21 | 16.9 | 14.8 | 13.6
22 | 16.8 | 14.1 | 13.5
23 | 16.9 | 13.1 | 12.8
0 | 17 | 12.9 | 12.2
1 | 16.9 | 13 | 9.7
2 | 16.9 | 12.8 | 7.7
3 | 15.9 | 12.6 | 7.5
4 | 15.8 | 12.4 | 7.5
5 | 15.7 | 11.9 | 7.3
6 | 16.2 | 12.3 | 7.2
7 | 16.6 | 12.9 | 9.1
8 | 18.5 | 14.1 | 11
9 | 21 | 15.4 | 14.3
10 | 22.7 | 16.4 | 16.6
11 | 24 | 17.2 | 18.7
12 | 24.7 | 17.8 | 19.8
13 | 24.5 | 17.7 | 20.4
14 | 25 | 18.1 | 20.4
15 | 24.7 | 18 | 20.6
16 | 24.6 | 18.1 | 20.3
17 | 23.9 | 17.6 | 19.7
18 | 22.8 | 16.7 | 17.9
19 | 21.8 | 15.6 | 16.5
20 | 20.4 | 14.8 | 14.3
21 | 19.1 | 14.2 | 12.6
22 | 18.2 | 13.8 | 11.4
23 | 17.8 | 13.2 | 11.4
0 | 17.4 | 13 | 11.4
1 | 14.6 | 13.2 | 10.7
2 | 12.6 | 13 | 10.1
3 | 12.6 | 12.9 | 9.9
4 | 11.7 | 12.8 | 9.7
5 | 11.4 | 12.7 | 10
6 | 11.2 | 12.4 | 10.2
7 | 12.8 | 12.9 | 10.2
8 | 14.4 | 13.6 | 11.1
9 | 17.3 | 14.6 | 12.2
10 | 20.1 | 15.4 | 13.5
11 | 22.1 | 15.9 | 14.8
12 | 23.4 | 16.4 | 14.9
13 | 23.5 | 16.1 | 14.5
14 | 23.7 | 16.5 | 14.6
15 | 23.1 | 16.2 | 15.1
16 | 23.6 | 16.5 | 14.5
17 | 22.5 | 16 | 14.7
18 | 20.4 | 15.4 | 13.8
19 | 17.6 | 14.7 | 12.8
20 | 16.9 | 14.2 | 12.5
21 | 15.8 | 13.9 | 11.8
22 | 15.5 | 13.7 | 11.8
23 | 14.7 | 13.2 | 11.5
0 | 13.8 | 11.9 | 11.2
1 | 11.5 | 12.1 | 10.9
2 | 9.8 | 11.9 | 10.7
3 | 9 | 11.7 | 10
4 | 9.5 | 11.6 | 9.6
5 | 8.5 | 11.6 | 9.1
6 | 7.6 | 11.2 | 9.7
7 | 10 | 11.8 | 10.2
8 | 12.4 | 12.5 | 11.1
9 | 15.7 | 13.5 | 14.2
10 | 18.3 | 14.4 | 15.6
11 | 21.1 | 15 | 17.1
12 | 22.9 | 15.4 | 18.5
13 | 23 | 15.4 | 18.1
14 | 23.5 | 15.6 | 18.6
15 | 23.2 | 15.2 | 18.2
16 | 23.4 | 15.6 | 18.5
17 | 21.5 | 15.1 | 17.6
18 | 19.8 | 14.4 | 16.3
19 | 15.5 | 13.6 | 14.8
20 | 14.7 | 13.1 | 13.6
21 | 14.1 | 12.9 | 13.2
22 | 12.8 | 12.6 | 11.8
23 | 12.7 | 12 | 11.9
0 | 12.5 | 12.1 | 12
1 | 12.4 | 12.3 | 11.3
2 | 11.9 | 12.1 | 10.9
3 | 11.2 | 12 | 10.3
4 | 11 | 12 | 10.3
5 | 10.6 | 11.9 | 10.1
6 | 11.4 | 11.6 | 9.9
7 | 12.1 | 12.1 | 10.6
8 | 14 | 12.7 | 11.3
9 | 16.8 | 13.5 | 13.4
10 | 18.8 | 14.2 | 15.3
11 | 20.5 | 14.7 | 15.8
12 | 22 | 15.1 | 16.6
13 | 21.7 | 14.7 | 16.6
14 | 22 | 15.2 | 16.9
15 | 21.8 | 15.1 | 16.4
16 | 21.9 | 15.2 | 16.8
17 | 21.3 | 14.8 | 16.8
18 | 19 | 14.2 | 15.2
19 | 17 | 13.6 | 13.8
20 | 15.7 | 13.2 | 12.8
21 | 15 | 13 | 12.3
22 | 13.9 | 12.7 | 12.2
23 | 13.6 | 12.3 | 12.2
0 | 13.2 | 8.7 | 12.1
1 | 11 | 9 | 11.9
2 | 9.3 | 8.7 | 11.5
3 | 8.6 | 8.5 | 11.5
4 | 7.8 | 8.4 | 11.4
5 | 7.9 | 8.3 | 11.1
6 | 8 | 7.8 | 10.8
7 | 8.3 | 8.6 | 11.4
8 | 11.4 | 9.6 | 12
9 | 13.5 | 10.9 | 13.8
10 | 15.6 | 12 | 15.2
11 | 17.2 | 12.8 | 16
12 | 18.9 | 13.4 | 16.5
13 | 18.6 | 13.2 | 16.5
14 | 19 | 13.6 | 16.7
15 | 18.9 | 13.1 | 16.2
16 | 18.9 | 13.6 | 16.5
17 | 18 | 12.9 | 16.4
18 | 15.5 | 12 | 15.5
19 | 13.9 | 11 | 14.4
20 | 13.3 | 10.4 | 13.4
21 | 12.6 | 10 | 12.5
22 | 11.2 | 9.7 | 12.4
23 | 11.3 | 8.9 | 12.8
0 | 11.4 | 8.4 | 13.2
1 | 10.6 | 8.8 | 13.5
2 | 10.1 | 8.5 | 13.7
3 | 9.6 | 8.2 | 13.4
4 | 9.4 | 8.1 | 13
5 | 9.2 | 7.9 | 13.3
6 | 9.5 | 7.2 | 13.6
7 | 9.7 | 8.3 | 13.4
8 | 12 | 9.6 | 13.6
9 | 14.2 | 11.3 | 15.2
10 | 16.2 | 12.8 | 15.6
11 | 17.1 | 13.8 | 16.3
12 | 18 | 14.6 | 16.8
13 | 17.7 | 14.5 | 17.1
14 | 18.1 | 14.9 | 17.2
15 | 17.8 | 14.5 | 16.9
16 | 17.8 | 14.9 | 17.1
17 | 17.7 | 14 | 16.8
18 | 16.4 | 12.8 | 16.3
19 | 14.5 | 11.5 | 15.4
20 | 13.5 | 10.7 | 15.3
21 | 12.3 | 10.2 | 14.3
22 | 10.9 | 9.7 | 14.6
23 | 11.7 | 8.7 | 14.5
0 | 12.5 | 11.7 | 14.5
1 | 12.2 | 11.9 | 13.1
2 | 12.1 | 11.7 | 12.1
3 | 11.8 | 11.6 | 11.9
4 | 12 | 11.5 | 11.7
5 | 11.9 | 11.4 | 11.5
6 | 11.8 | 11 | 11.6
7 | 12.5 | 11.6 | 11.7
8 | 13.2 | 12.4 | 13.3
9 | 13.8 | 13.5 | 14.4
10 | 14.3 | 14.4 | 16.4
11 | 14.8 | 15.1 | 16.7
12 | 14.4 | 15.6 | 17.4
13 | 14.8 | 15.7 | 16.9
14 | 14.6 | 15.8 | 17.5
15 | 14.9 | 15.3 | 17.4
16 | 14.6 | 15.8 | 17.2
17 | 14.8 | 15.2 | 17
18 | 13.9 | 14.4 | 16.4
19 | 13.7 | 13.6 | 14.8
20 | 13.2 | 13.1 | 14.4
21 | 12.5 | 12.8 | 13.7
22 | 12.8 | 12.5 | 13
23 | 12.5 | 11.9 | 12.9
0 | 12.3 | 11.7 | 12.8
1 | 11.1 | 12.2 | 11.3
2 | 10 | 11.8 | 10.2
3 | 10.2 | 11.5 | 9.4
4 | 10.2 | 11.3 | 9.5
5 | 10.1 | 11.1 | 9
6 | 9.9 | 10.3 | 8.4
7 | 10.6 | 11.6 | 10
8 | 11.3 | 13.2 | 11.5
9 | 13.1 | 15.3 | 13.8
10 | 14 | 17 | 16.8
11 | 14.9 | 18.3 | 18.4
12 | 15.9 | 19.3 | 19.1
13 | 16.3 | 19.1 | 19.7
14 | 16.2 | 19.6 | 19.8
15 | 16.2 | 19.5 | 20
16 | 16.2 | 19.6 | 19.6
17 | 16.3 | 18.6 | 19.2
18 | 14.7 | 17 | 17.1
19 | 13.9 | 15.5 | 14.8
20 | 13.1 | 14.5 | 13.7
21 | 12.6 | 13.9 | 12.5
22 | 10.9 | 13.3 | 12.1
23 | 12.1 | 12.1 | 12
0 | 13.2 | 10.1 | 12
1 | 13.1 | 10.6 | 11.2
2 | 12.6 | 10.2 | 10.6
3 | 12.8 | 9.8 | 10.5
4 | 12.5 | 9.6 | 10.1
5 | 12.1 | 9.4 | 9.7
6 | 12.4 | 8.4 | 9.5
7 | 12.5 | 9.9 | 9.3
8 | 14.3 | 11.8 | 11.4
9 | 16.7 | 14.3 | 13.6
10 | 18 | 16.4 | 15.9
11 | 19.8 | 17.9 | 17.7
12 | 20.2 | 19 | 18.2
13 | 20.3 | 19 | 18.2
14 | 20.2 | 19.4 | 18.7
15 | 20.4 | 19.1 | 18.6
16 | 20.3 | 19.4 | 18.5
17 | 20.3 | 18.2 | 18.6
18 | 18.7 | 16.4 | 16
19 | 17.5 | 14.6 | 14
20 | 15.7 | 13.4 | 13.7
21 | 15.2 | 12.6 | 12.9
22 | 14.8 | 12 | 12.3
23 | 15.3 | 10.5 | 12.4
0 | 15.8 | 7.8 | 12.6
1 | 16.3 | 8.2 | 12.1
2 | 16.7 | 7.8 | 11.8
3 | 16.1 | 7.5 | 11.9
4 | 16.2 | 7.4 | 11.6
5 | 16.1 | 7.2 | 11.3
6 | 15.8 | 6.3 | 11.1
7 | 16.5 | 7.6 | 12.4
8 | 17.1 | 9.2 | 13.7
9 | 18 | 11.2 | 14.6
10 | 19.6 | 13 | 15.6
11 | 20.2 | 14.3 | 17.1
12 | 20.7 | 15.2 | 18.4
13 | 20.4 | 15.4 | 18.3
14 | 20.3 | 15.5 | 18.6
15 | 20.7 | 15.3 | 18.3
16 | 20.6 | 15.5 | 18.2
17 | 20.3 | 14.5 | 17.9
18 | 19.9 | 13 | 17.2
19 | 18.9 | 11.5 | 15.6
20 | 17.7 | 10.5 | 14.7
21 | 17.7 | 9.9 | 14.6
22 | 17.1 | 9.3 | 13.6
23 | 16.8 | 8.1 | 13.4
0 | 16.5 | 8.8 | 13.2
1 | 14.8 | 9.3 | 11.6
2 | 13.7 | 8.8 | 10.6
3 | 13.4 | 8.4 | 9.7
4 | 13.1 | 8.2 | 9.8
5 | 13.3 | 8 | 9.9
6 | 13.6 | 6.9 | 10
7 | 13.7 | 8.5 | 10
8 | 14.4 | 10.6 | 11.8
9 | 16.4 | 13.2 | 12.6
10 | 17.8 | 15.5 | 14
11 | 19 | 17.1 | 15
12 | 19.2 | 18.4 | 15.3
13 | 19.2 | 18.7 | 15.7
14 | 18.9 | 18.8 | 15.7
15 | 19.5 | 18.5 | 15.4
16 | 18.9 | 18.8 | 15.1
17 | 19.1 | 17.5 | 15
18 | 18.3 | 15.5 | 13.6
19 | 16.6 | 13.5 | 13
20 | 16 | 12.2 | 12.6
21 | 15.7 | 11.4 | 12.4
22 | 15.2 | 10.7 | 11.2
23 | 15.3 | 9.2 | 11.3
0 | 15.5 | 8.6 | 11.5
1 | 14.9 | 9.2 | 10.7
2 | 14.3 | 8.7 | 9.7
3 | 15 | 8.3 | 9.3
4 | 14.4 | 8.1 | 8.7
5 | 13.9 | 7.9 | 9
6 | 14.1 | 6.8 | 9.1
7 | 14.3 | 8.4 | 10.1
8 | 15.5 | 10.4 | 11.7
9 | 16.8 | 12.9 | 13.4
10 | 18.2 | 15.1 | 15.2
11 | 18.9 | 16.6 | 17
12 | 19.3 | 17.9 | 17.9
13 | 19.8 | 17.9 | 18.3
14 | 19.3 | 18.2 | 18.4
15 | 19.7 | 18.1 | 18.2
16 | 19.6 | 18.2 | 18.3
17 | 19.4 | 17 | 17.8
18 | 18 | 15.1 | 16
19 | 17.2 | 13.2 | 14.6
20 | 16.7 | 12 | 13.2
21 | 16.1 | 11.2 | 12.7
22 | 15.7 | 10.5 | 11.8
23 | 15.7 | 9 | 13.4
0 | 15.7 | 8.6 | 14.9
1 | 15.1 | 9.2 | 15.4
2 | 14.5 | 8.7 | 15.7
3 | 15 | 8.3 | 15.8
4 | 14.7 | 8.1 | 15.8
5 | 14.4 | 7.9 | 15.5
6 | 14.7 | 6.8 | 15.3
7 | 14.9 | 8.4 | 14.9
8 | 15.9 | 10.4 | 16.5
9 | 16.2 | 13 | 17.9
10 | 17.7 | 15.2 | 19.3
11 | 18 | 16.8 | 20.1
12 | 18.9 | 18 | 20.5
13 | 18.4 | 17.9 | 21.1
14 | 18.7 | 18.4 | 20.7
15 | 18.8 | 18.3 | 21.1
16 | 18.3 | 18.4 | 21
17 | 18.6 | 17.1 | 20.6
18 | 18.3 | 15.2 | 20.1
19 | 16.3 | 13.3 | 18.6
20 | 16.4 | 12 | 18.2
21 | 16.6 | 11.2 | 17.2
22 | 16 | 10.6 | 17.1
23 | 15.8 | 9 | 16.9
0 | 15.5 | 11.8 | 16.7
1 | 14.1 | 12.1 | 15.4
2 | 13.3 | 11.9 | 14.5
3 | 13.6 | 11.7 | 14.1
4 | 12.8 | 11.6 | 13.6
5 | 12 | 11.4 | 13.1
6 | 12.3 | 10.9 | 13.3
7 | 12.5 | 11.7 | 13.6
8 | 15.6 | 12.8 | 15.4
9 | 18.2 | 14.2 | 17.3
10 | 20.1 | 15.4 | 18.3
11 | 21.2 | 16.3 | 20
12 | 22.4 | 16.9 | 21.4
13 | 23 | 16.7 | 21.3
14 | 23.2 | 17.1 | 21
15 | 22.8 | 16.7 | 20.9
16 | 22.9 | 17.1 | 21.4
17 | 22.7 | 16.4 | 20.9
18 | 20.8 | 15.4 | 19.5
19 | 18.5 | 14.4 | 18
20 | 16.9 | 13.7 | 16.7
21 | 16.6 | 13.3 | 16
22 | 15.3 | 12.9 | 15.5
23 | 15.6 | 12.1 | 14.5
0 | 15.9 | 9.8 | 13.4
1 | 15 | 10 | 10.4
2 | 14.1 | 9.8 | 7.9
3 | 14 | 9.5 | 8
4 | 13.8 | 9.4 | 7.5
5 | 13.6 | 9.3 | 6.8
6 | 13.9 | 8.7 | 6.2
7 | 14.3 | 9.6 | 8.1
8 | 16.3 | 10.8 | 10
9 | 18.4 | 12.3 | 14.1
10 | 19.9 | 13.6 | 17.2
11 | 20.5 | 14.5 | 20
12 | 21.6 | 15.3 | 21.3
13 | 21.7 | 15.4 | 21.8
14 | 21.3 | 15.5 | 21.9
15 | 21.6 | 15.2 | 21.6
16 | 21.3 | 15.5 | 21.5
17 | 20.7 | 14.7 | 20
18 | 19.6 | 13.6 | 17.8
19 | 18.2 | 12.5 | 15.3
20 | 17.3 | 11.7 | 13.7
21 | 16.5 | 11.3 | 12.2
22 | 16.2 | 10.9 | 11.2
23 | 15.4 | 10 | 10.5
0 | 14.6 | 11.5 | 9.8
1 | 12.2 | 11.8 | 8.7
2 | 10.7 | 11.5 | 7.4
3 | 10.3 | 11.3 | 7.3
4 | 10.4 | 11.2 | 6.6
5 | 10.2 | 11.1 | 6.1
6 | 10 | 10.6 | 5.6
7 | 11.2 | 11.4 | 7.7
8 | 12.4 | 12.3 | 9.7
9 | 13.8 | 13.6 | 13.4
10 | 15.2 | 14.6 | 17.2
11 | 16.3 | 15.4 | 19.2
12 | 17.5 | 16 | 20.9
13 | 17.4 | 16 | 21.4
14 | 17.2 | 16.2 | 21.5
15 | 17.2 | 15.9 | 21.2
16 | 17.7 | 16.2 | 21.2
17 | 16.6 | 15.5 | 20.6
18 | 15.9 | 14.6 | 17.3
19 | 14.6 | 13.7 | 15.2
20 | 13.2 | 13.1 | 13.6
21 | 13.3 | 12.7 | 11.6
22 | 12.5 | 12.4 | 10.7
23 | 12.8 | 11.6 | 11.7
0 | 13.1 | 10.9 | 12.6
1 | 13.3 | 10.1 | 13.6
2 | 13.6 | 9.3 | 14.6
3 | 13.1 | 9.2 | 13.8
4 | 12.6 | 9.1 | 14.5
5 | 12.6 | 9.1 | 13.8
6 | 12.6 | 8.4 | 13.1
7 | 13 | 9 | 14.3
8 | 13.5 | 9.7 | 15.5
9 | 14.9 | 10.8 | 16.5
10 | 15.6 | 11.9 | 18.4
11 | 15.7 | 12.8 | 20.7
12 | 16.1 | 13.3 | 20.7
13 | 16.3 | 13 | 20.5
14 | 16.5 | 13.2 | 20.5
15 | 16.2 | 12.7 | 20.8
16 | 16.1 | 13.2 | 20.4
17 | 16.2 | 12.4 | 19.6
18 | 15.4 | 11.5 | 18.5
19 | 14.8 | 10.9 | 17.1
20 | 14.1 | 10.5 | 17.2
21 | 14.3 | 10.2 | 15.7
22 | 12.9 | 9.9 | 14.9
23 | 13.8 | 9.1 | 15.2
0 | 14.7 | 12.2 | 15.5
1 | 14.4 | 12.5 | 15.1
2 | 14.3 | 12.4 | 14.8
3 | 13.8 | 12.3 | 15.4
4 | 13.2 | 12.2 | 14.9
5 | 13.5 | 12.2 | 15.4
6 | 13.8 | 11.9 | 14.8
7 | 13.9 | 12.2 | 14.2
8 | 14.4 | 12.5 | 15.3
9 | 16.1 | 13.1 | 16.4
10 | 17.7 | 13.8 | 18.4
11 | 18.6 | 14.2 | 19.1
12 | 18.8 | 14.5 | 19.3
13 | 19.3 | 14.4 | 19.4
14 | 18.8 | 14.5 | 18.9
15 | 19.2 | 14.3 | 19.2
16 | 19 | 14.5 | 19
17 | 18.2 | 14 | 18.7
18 | 18.2 | 13.6 | 17.9
19 | 16.8 | 13.2 | 16.9
20 | 16 | 13 | 16.1
21 | 15.5 | 12.8 | 16
22 | 14.9 | 12.7 | 15.8
23 | 14.8 | 12.3 | 15.4
0 | 14.7 | 10.1 | 15
1 | 13.6 | 10.6 | 13.6
2 | 12.6 | 10.4 | 12.5
3 | 12.2 | 10.2 | 11.7
4 | 12.3 | 10.2 | 11.5
5 | 11.9 | 10.1 | 11.1
6 | 11.4 | 9.3 | 10.6
7 | 12.6 | 10 | 11.4
8 | 13.8 | 10.7 | 12.2
9 | 15.3 | 11.9 | 14.9
10 | 17.9 | 13.1 | 16.9
11 | 19.7 | 14 | 18.1
12 | 20 | 14.6 | 19.3
13 | 20.2 | 14.2 | 19.3
14 | 19.9 | 14.6 | 19.1
15 | 19.8 | 14.5 | 19.5
16 | 19.7 | 14.5 | 19.5
17 | 19.5 | 13.7 | 18.6
18 | 17.6 | 12.7 | 16.7
19 | 16.3 | 12 | 15.7
20 | 15.6 | 11.6 | 13.9
21 | 14.7 | 11.3 | 14
22 | 14.1 | 11 | 13.4
23 | 13.9 | 10.1 | 13.1
0 | 13.7 | 9.8 | 12.9
1 | 12.8 | 10.5 | 12.3
2 | 12.2 | 10.2 | 11.4
3 | 11.7 | 10 | 11.5
4 | 12 | 10 | 11.7
5 | 12.3 | 9.9 | 11.3
6 | 12 | 8.9 | 10.8
7 | 12.4 | 9.8 | 12
8 | 12.3 | 10.6 | 13.2
9 | 13.2 | 12.1 | 14.9
10 | 14.4 | 13.5 | 15.8
11 | 15.2 | 14.7 | 17.9
12 | 15 | 15.4 | 18.2
13 | 14.9 | 14.9 | 18
14 | 15.5 | 15.3 | 18.1
15 | 14.9 | 14.9 | 18.3
16 | 15.3 | 15.2 | 17.8
17 | 15.1 | 14.2 | 17.4
18 | 14.5 | 13.1 | 16.7
19 | 13.1 | 12.2 | 14.9
20 | 13.2 | 11.7 | 13.6
21 | 13.8 | 11.3 | 13.5
22 | 12.8 | 10.9 | 12.9
23 | 13.4 | 9.9 | 12.6
0 | 14.1 | 11 | 12.3
1 | 13.9 | 11.3 | 10.8
2 | 13.8 | 11.2 | 10.2
3 | 13.3 | 11.1 | 8.9
4 | 13.1 | 11.1 | 9.3
5 | 12.8 | 11 | 9
6 | 12.6 | 10.5 | 8.7
7 | 13 | 11 | 9.3
8 | 13.3 | 11.4 | 10
9 | 14.8 | 12.2 | 10.6
10 | 15.9 | 13 | 11.5
11 | 16.7 | 13.6 | 13
12 | 17.1 | 14 | 12.8
13 | 16.7 | 13.7 | 12.8
14 | 17.2 | 13.9 | 12.9
15 | 17 | 13.6 | 13
16 | 17.2 | 13.9 | 12.7
17 | 16.7 | 13.3 | 11.8
18 | 16 | 12.7 | 11.3
19 | 14.7 | 12.3 | 11.5
20 | 14.4 | 12 | 9.7
21 | 14.1 | 11.8 | 10.6
22 | 13.4 | 11.6 | 9.7
23 | 13.2 | 11.1 | 9.5
0 | 13 | 8.3 | 9.3
1 | 11.2 | 9.2 | 8.4
2 | 10 | 8.9 | 7.9
3 | 8.8 | 8.5 | 7.4
4 | 9.1 | 8.4 | 6.8
5 | 9.4 | 8.3 | 7
6 | 9.6 | 7 | 7.1
7 | 10.3 | 8.3 | 7.2
8 | 10.8 | 9.5 | 8.3
9 | 13.9 | 11.6 | 10.4
10 | 16.8 | 13.8 | 12.1
11 | 17.4 | 15.5 | 13.6
12 | 18.6 | 16.5 | 13.7
13 | 18.6 | 16.3 | 13.5
14 | 18.2 | 16.4 | 13.8
15 | 18.7 | 16.4 | 13.6
16 | 18.5 | 16.3 | 13.6
17 | 16.5 | 14.8 | 13.3
18 | 15.5 | 13.1 | 12
19 | 14.6 | 11.8 | 10.8
20 | 13 | 11.1 | 10.2
21 | 12.1 | 10.5 | 9.3
22 | 11.1 | 9.9 | 8.6
23 | 11.5 | 8.4 | 8
0 | 11.9 | 10.2 | 7.3
1 | 11 | 11.1 | 5.7
2 | 10.3 | 10.7 | 4.3
3 | 10.3 | 10.4 | 4.8
4 | 10.1 | 10.3 | 4.1
5 | 10 | 10.2 | 3.6
6 | 10 | 8.9 | 3
7 | 10 | 10.2 | 4.6
8 | 10.2 | 11.3 | 6.1
9 | 11.5 | 13.3 | 7.6
10 | 11.7 | 15.4 | 10
11 | 12.7 | 17 | 11.9
12 | 12.4 | 18 | 12.7
13 | 12.1 | 17.8 | 12.9
14 | 12.7 | 17.8 | 12.6
15 | 12.3 | 17.7 | 12.4
16 | 12.3 | 17.7 | 12.8
17 | 12.4 | 16.3 | 11
18 | 11.9 | 14.7 | 9.9
19 | 11.3 | 13.5 | 7.8
20 | 11.5 | 12.8 | 7.2
21 | 11 | 12.3 | 6.8
22 | 10.5 | 11.7 | 5.5
23 | 12.8 | 10.3 | 7
0 | 15.1 | 11.7 | 8.5
1 | 15.1 | 12.1 | 9.2
2 | 15.1 | 12 | 9
3 | 15.3 | 11.8 | 8.5
4 | 15.6 | 11.8 | 9
5 | 15.5 | 11.7 | 9.3
6 | 15.2 | 11 | 10.4
7 | 15.6 | 11.7 | 9.5
8 | 15.3 | 12.3 | 10.9
9 | 15.8 | 13.3 | 12.5
10 | 16.4 | 14.4 | 14.3
11 | 16.2 | 15.2 | 15.3
12 | 16.3 | 15.7 | 16.3
13 | 16.1 | 15.3 | 16.2
14 | 16.6 | 15.6 | 16.4
15 | 16.5 | 15.4 | 16.1
16 | 16.3 | 15.6 | 16.3
17 | 16.2 | 14.8 | 15.7
18 | 16 | 14 | 14.1
19 | 16.2 | 13.4 | 12.8
20 | 15.6 | 13.1 | 12.2
21 | 15.2 | 12.8 | 11.5
22 | 15.6 | 12.5 | 11.5
23 | 15.6 | 11.7 | 12.9
0 | 15.5 | 12.6 | 14.2
1 | 15.1 | 13.1 | 14.4
2 | 14.7 | 12.9 | 14.3
3 | 15.1 | 12.8 | 14.2
4 | 14.9 | 12.7 | 14.5
5 | 14.9 | 12.7 | 14.8
6 | 14.8 | 12 | 14.3
7 | 15 | 12.6 | 14.7
8 | 14.8 | 13.2 | 14.3
9 | 16.1 | 14.2 | 15.1
10 | 16.8 | 15.3 | 15.4
11 | 17 | 16.1 | 15.3
12 | 17.5 | 16.6 | 15.2
13 | 17.4 | 16.1 | 15.8
14 | 17.4 | 16.5 | 15.8
15 | 17.6 | 16.1 | 15.8
16 | 17 | 16.5 | 15.5
17 | 17.3 | 15.8 | 15.3
18 | 16.9 | 15 | 15.6
19 | 16.3 | 14.4 | 14.8
20 | 16.9 | 14 | 15.2
21 | 15.8 | 13.7 | 14.6
22 | 14.6 | 13.4 | 14.6
23 | 15 | 12.7 | 14.2
0 | 15.4 | 12 | 13.7
1 | 14.4 | 12.9 | 12.2
2 | 14.1 | 12.6 | 10.9
3 | 13.1 | 12.3 | 10.6
4 | 12.2 | 12.2 | 10.6
5 | 12.4 | 12.1 | 10.1
6 | 12.5 | 10.8 | 9.5
7 | 13 | 12 | 10.5
8 | 14.3 | 13.2 | 11.5
9 | 16.3 | 15.2 | 14.5
10 | 17.3 | 17.3 | 16.2
11 | 18.8 | 18.9 | 18.2
12 | 19.1 | 19.9 | 18.9
13 | 19.3 | 19.7 | 18.7
14 | 19.4 | 19.7 | 18.6
15 | 18.9 | 19.7 | 19
16 | 19.1 | 19.7 | 18.7
17 | 17.8 | 18.2 | 18.1
18 | 16.7 | 16.6 | 15.7
19 | 16.3 | 15.4 | 14.3
20 | 15.3 | 14.7 | 13.7
21 | 14.7 | 14.2 | 13.4
22 | 14.6 | 13.6 | 12.4
23 | 14 | 12.2 | 11.6
0 | 13.4 | 11.3 | 10.8
1 | 12 | 12.5 | 9.2
2 | 11.1 | 12 | 7.7
3 | 10.5 | 11.6 | 6.7
4 | 10.9 | 11.5 | 7.3
5 | 10.5 | 11.4 | 6.8
6 | 10.1 | 9.6 | 6.3
7 | 11 | 11.3 | 7.3
8 | 12 | 12.8 | 8.3
9 | 13.1 | 15.4 | 10.6
10 | 15 | 18.2 | 13.5
11 | 16.4 | 20.2 | 15.3
12 | 16.8 | 21.6 | 15.5
13 | 16.6 | 21.2 | 15.7
14 | 16.9 | 21.3 | 15.7
15 | 16.3 | 21.3 | 15.8
16 | 16.4 | 21.3 | 15.3
17 | 16.5 | 19.4 | 14.9
18 | 14.4 | 17.3 | 13.2
19 | 14 | 15.7 | 11
20 | 13.5 | 14.8 | 10.7
21 | 12 | 14.1 | 9.7
22 | 11.9 | 13.3 | 9.5
23 | 12.3 | 11.4 | 10.9
0 | 12.6 | 16.1 | 12.4
1 | 12.2 | 17.1 | 12.8
2 | 11.1 | 16.7 | 13.1
3 | 9.9 | 16.4 | 13.9
4 | 10.7 | 16.3 | 13.7
5 | 11.4 | 16.2 | 13.1
6 | 10.9 | 14.6 | 12.4
7 | 11.5 | 16.1 | 13.6
8 | 12.8 | 17.4 | 14.6
9 | 15.5 | 19.7 | 16.3
10 | 17.5 | 22.2 | 17.8
11 | 19.6 | 24 | 18.3
12 | 20.4 | 25.2 | 19.1
13 | 20.7 | 24.8 | 19
14 | 20.5 | 25 | 19.2
15 | 20.6 | 24.8 | 19
16 | 20.6 | 24.9 | 19.1
17 | 18.6 | 23.2 | 18
18 | 17.7 | 21.4 | 17.5
19 | 15.9 | 20 | 16.1
20 | 15.1 | 19.2 | 15.3
21 | 13.8 | 18.6 | 15
22 | 13.2 | 17.9 | 14.2
23 | 13.4 | 16.2 | 13.8
0 | 13.6 | 15.7 | 13.3
1 | 13.9 | 16.3 | 12
2 | 13.6 | 16.1 | 11.2
3 | 14.2 | 15.8 | 11
4 | 13.5 | 15.8 | 10.3
5 | 12.5 | 15.7 | 10.1
6 | 13.3 | 14.8 | 9.8
7 | 13.9 | 15.7 | 10.7
8 | 15.3 | 16.5 | 11.5
9 | 17.8 | 17.9 | 13.6
10 | 20.2 | 19.4 | 15.3
11 | 21.9 | 20.5 | 16.2
12 | 22.8 | 21.2 | 17.4
13 | 22.7 | 20.6 | 17.3
14 | 22.9 | 21.1 | 17.2
15 | 22.8 | 21 | 17.4
16 | 22.8 | 21 | 16.9
17 | 21.7 | 20 | 16.4
18 | 20.1 | 18.9 | 15.1
19 | 18.1 | 18 | 13.8
20 | 17.1 | 17.6 | 13.3
21 | 17 | 17.2 | 12.9
22 | 15.9 | 16.8 | 11.8
23 | 14.6 | 15.7 | 11.4
0 | 13.4 | 14.3 | 11
1 | 10.3 | 14.5 | 9.1
2 | 8.5 | 14.4 | 7.3
3 | 7.8 | 14.3 | 7.7
4 | 7.2 | 14.3 | 7.9
5 | 6.9 | 14.3 | 6.9
6 | 7.3 | 14.1 | 5.9
7 | 7.8 | 14.3 | 7.2
8 | 9.4 | 14.5 | 8.6
9 | 12 | 14.9 | 11.7
10 | 13.9 | 15.4 | 14.4
11 | 15.4 | 15.7 | 16
12 | 16.2 | 15.9 | 17.1
13 | 16.1 | 15.6 | 17.3
14 | 16.7 | 15.9 | 17.6
15 | 16.1 | 15.6 | 17.3
16 | 16.3 | 15.8 | 17.6
17 | 15.6 | 15.5 | 16.2
18 | 13.4 | 15.2 | 13.6
19 | 11.9 | 15 | 12.3
20 | 11.6 | 14.8 | 11.1
21 | 10.1 | 14.7 | 10.2
22 | 9.1 | 14.6 | 9.5
23 | 9.4 | 14.3 | 9.1
0 | 9.7 | 10.5 | 8.6
1 | 8.8 | 11.4 | 7.9
2 | 8.2 | 11 | 7.6
3 | 8 | 10.7 | 6.8
4 | 7.8 | 10.6 | 6.5
5 | 7.5 | 10.5 | 6.2
6 | 7.7 | 9.2 | 6.7
7 | 7.9 | 10.5 | 7.3
8 | 8.6 | 11.6 | 7.8
9 | 10.3 | 13.6 | 10
10 | 11.6 | 15.6 | 12.2
11 | 12.3 | 17.2 | 13.1
12 | 12.6 | 18.1 | 13.8
13 | 12.9 | 17.9 | 14
14 | 12.5 | 18 | 14
15 | 13 | 17.7 | 13.9
16 | 12.7 | 17.9 | 13.7
17 | 12.5 | 16.5 | 13.2
18 | 11.1 | 14.9 | 11.8
19 | 11.2 | 13.8 | 10.3
20 | 9.7 | 13.1 | 9.6
21 | 8.7 | 12.6 | 9.3
22 | 9.8 | 12 | 8.8
23 | 9.7 | 10.6 | 8.4
0 | 9.6 | 4.4 | 7.9
1 | 9.1 | 6.3 | 7.1
2 | 8.1 | 6.1 | 6.4
3 | 7.4 | 5.9 | 5.6
4 | 8.2 | 5.8 | 5.8
5 | 7.5 | 5.8 | 6
6 | 7.3 | 5.7 | 5.9
7 | 6.9 | 5.7 | 6.7
8 | 6.5 | 6.2 | 6.9
9 | 9.6 | 7.7 | 6.9
10 | 12.7 | 9.6 | 9.1
11 | 14.6 | 11.3 | 10.9
12 | 14.7 | 11.8 | 10.8
13 | 14.6 | 11.6 | 11
14 | 14.8 | 11.9 | 10.9
15 | 14.7 | 12 | 10.9
16 | 14.4 | 11.6 | 10.9
17 | 13.6 | 10.2 | 10.9
18 | 12 | 9 | 9.3
19 | 10.3 | 8.2 | 8.6
20 | 10.6 | 7.7 | 8
21 | 9.7 | 7.3 | 7.2
22 | 9 | 7 | 7.6
23 | 8.4 | 5.5 | 7.4
0 | 7.8 | 3.5 | 7.1
1 | 6.6 | 5.5 | 6.7
2 | 5.9 | 5.3 | 6.5
3 | 4.3 | 5.1 | 6.4
4 | 5.1 | 5 | 6.5
5 | 4 | 4.9 | 5.9
6 | 3 | 4.8 | 5.6
7 | 4.2 | 4.8 | 5.3
8 | 5.5 | 5.4 | 6.8
9 | 7.8 | 6.9 | 8.3
10 | 10.5 | 8.9 | 9.8
11 | 14 | 10.6 | 11.2
12 | 14.2 | 11 | 11.5
13 | 14.4 | 10.9 | 11.6
14 | 14.5 | 11.2 | 11.9
15 | 14.4 | 10.9 | 11.5
16 | 14.2 | 11 | 11.7
17 | 11.9 | 9.5 | 10.2
18 | 9.5 | 8.2 | 9.3
19 | 9.8 | 7.4 | 8.8
20 | 8.9 | 6.9 | 8.4
21 | 7.7 | 6.5 | 7.6
22 | 6.8 | 6.1 | 8
23 | 6.5 | 4.7 | 8.7
0 | 6.2 | 4.6 | 9.4
1 | 6.9 | 6.7 | 10.1
2 | 7.5 | 6.5 | 10.4
3 | 6.6 | 6.3 | 10.9
4 | 7.3 | 6.2 | 9.6
5 | 6.8 | 6.1 | 10.3
6 | 6.1 | 6 | 9.9
7 | 6.6 | 6 | 9.2
8 | 6.9 | 6.6 | 10.6
9 | 9.8 | 8.2 | 11.9
10 | 11.5 | 10.4 | 15.1
11 | 13.3 | 12.2 | 15.5
12 | 13.3 | 12.9 | 15.7
13 | 13.1 | 12.9 | 16
14 | 13.3 | 12.9 | 16.1
15 | 13.4 | 12.9 | 16
16 | 13.3 | 12.6 | 15.8
17 | 12.5 | 11 | 14.5
18 | 11.6 | 9.7 | 13.8
19 | 9.7 | 8.8 | 13.1
20 | 9.5 | 8.3 | 12.2
21 | 9.5 | 7.8 | 12.9
22 | 9.6 | 7.4 | 12.2
23 | 9 | 5.9 | 11.4
0 | 8.3 | 8.1 | 10.5
1 | 8.4 | 9.1 | 9.6
2 | 8.2 | 9 | 8.9
3 | 6.9 | 8.9 | 9.2
4 | 7.6 | 8.8 | 8.3
5 | 6.8 | 8.8 | 8.8
6 | 5.9 | 8.7 | 8
7 | 6.9 | 8.7 | 7.2
8 | 7.8 | 9 | 9.1
9 | 10.4 | 9.8 | 11
10 | 13.7 | 10.8 | 13.1
11 | 15.9 | 11.7 | 15
12 | 16.6 | 11.5 | 15.3
13 | 16.7 | 11.7 | 15
14 | 16.8 | 11.9 | 15.4
15 | 16.7 | 11.5 | 15.1
16 | 16.7 | 11.8 | 15.3
17 | 15.3 | 11.1 | 14.4
18 | 12.1 | 10.5 | 12.2
19 | 11.4 | 10 | 11.9
20 | 11.3 | 9.8 | 10.1
21 | 10.6 | 9.6 | 9.9
22 | 10.1 | 9.4 | 9.2
23 | 10.1 | 8.6 | 9.6
0 | 10.1 | 7.8 | 10
1 | 10.1 | 9.1 | 9.8
2 | 9.8 | 9 | 9.9
3 | 8.7 | 8.9 | 9.3
4 | 8.5 | 8.8 | 9.6
5 | 8.4 | 8.7 | 8.8
6 | 8.1 | 8.7 | 7.9
7 | 9 | 8.7 | 9.3
8 | 9.8 | 9.1 | 10.6
9 | 12.1 | 10.1 | 12.2
10 | 13.8 | 11.6 | 14.4
11 | 15.4 | 12.8 | 17.1
12 | 15.7 | 12.9 | 17.7
13 | 15.7 | 13.2 | 17.9
14 | 15.8 | 13.2 | 18
15 | 15.6 | 12.9 | 17.9
16 | 15.7 | 13 | 17.8
17 | 13.7 | 12 | 16.6
18 | 13.1 | 11.1 | 14.5
19 | 12.6 | 10.5 | 13.5
20 | 11.3 | 10.2 | 12.5
21 | 10.8 | 9.9 | 11.7
22 | 10.9 | 9.6 | 11.9
23 | 11.4 | 8.6 | 11.7
0 | 11.9 | 7.9 | 11.6
1 | 12.7 | 8.7 | 11.4
2 | 12.9 | 8.7 | 11.3
3 | 12.7 | 8.6 | 11.3
4 | 12.4 | 8.5 | 10.7
5 | 13.3 | 8.5 | 11
6 | 12.5 | 8.5 | 10.9
7 | 11.6 | 8.5 | 10.7
8 | 13.4 | 8.7 | 11.4
9 | 15.1 | 9.3 | 12.1
10 | 17.2 | 10.1 | 13.3
11 | 18.4 | 10.8 | 13.8
12 | 18.7 | 10.9 | 13.9
13 | 18.7 | 10.8 | 13.6
14 | 18.8 | 11.1 | 13.7
15 | 18.7 | 10.9 | 13.6
16 | 18.4 | 11 | 13.4
17 | 16.9 | 10.4 | 13.5
18 | 16 | 9.9 | 13
19 | 15.2 | 9.5 | 12.7
20 | 15.2 | 9.3 | 12.4
21 | 14.9 | 9.2 | 11.8
22 | 13.8 | 9 | 11.1
23 | 14.5 | 8.4 | 10.8
0 | 15.3 | 10.8 | 10.4
1 | 15.7 | 11 | 8.9
2 | 16.2 | 11 | 7.7
3 | 15.7 | 11 | 7.6
4 | 15.3 | 10.9 | 8.1
5 | 15.4 | 10.9 | 8.1
6 | 15.6 | 10.9 | 7.3
7 | 15.8 | 10.9 | 6.4
8 | 15.5 | 11 | 8
9 | 15.4 | 11.1 | 9.6
10 | 16.2 | 11.3 | 12.6
11 | 16.6 | 11.4 | 13.8
12 | 16.4 | 10.9 | 14.7
13 | 16.5 | 11.1 | 14.8
14 | 16.2 | 11.5 | 14.8
15 | 16.8 | 11.2 | 14.9
16 | 16.5 | 11.5 | 14.7
17 | 16.6 | 11.3 | 13.3
18 | 16.1 | 11.2 | 11.8
19 | 16.2 | 11.2 | 10.9
20 | 15.7 | 11.1 | 10.1
21 | 15.6 | 11.1 | 10.1
22 | 15.9 | 11 | 9.2
23 | 15.3 | 10.9 | 9.5
0 | 14.6 | 8.6 | 9.8
1 | 12.7 | 8.9 | 10.1
2 | 11.2 | 8.8 | 10.2
3 | 11.9 | 8.8 | 11
4 | 11 | 8.8 | 10.1
5 | 10.9 | 8.8 | 9.4
6 | 10.7 | 8.8 | 8.6
7 | 11.2 | 8.8 | 10
8 | 11.7 | 8.8 | 11.3
9 | 12.9 | 9 | 13.2
10 | 14.8 | 9.2 | 15.5
11 | 15.5 | 9.4 | 17.7
12 | 16.1 | 9.2 | 18.2
13 | 15.9 | 9.2 | 18.2
14 | 16.1 | 9.5 | 18.3
15 | 15.9 | 9 | 18.2
16 | 15.7 | 9.5 | 18.1
17 | 15.1 | 9.3 | 16.7
18 | 14.3 | 9.2 | 15.4
19 | 14.2 | 9.1 | 14.3
20 | 13.5 | 9 | 12.7
21 | 11.9 | 9 | 11.8
22 | 11.6 | 8.9 | 12.2
23 | 11.6 | 8.8 | 9.6
0 | 11.6 | 7.7 | 7
1 | 10.2 | 9.4 | 7.7
2 | 9.5 | 9.2 | 8.4
3 | 9.7 | 9.1 | 7.7
4 | 9.6 | 9 | 8.2
5 | 9.1 | 8.9 | 7.7
6 | 9.6 | 8.9 | 7.5
7 | 9 | 8.9 | 8
8 | 8.4 | 9.3 | 7.8
9 | 10.7 | 10.6 | 10.2
10 | 13 | 12.3 | 10.9
11 | 14.7 | 13.8 | 12.8
12 | 14.9 | 14.2 | 12.9
13 | 14.8 | 14.1 | 12.7
14 | 15 | 14.3 | 12.7
15 | 14.8 | 13.9 | 13
16 | 14.7 | 14.1 | 12.9
17 | 13.7 | 12.8 | 12
18 | 12.2 | 11.8 | 10.4
19 | 12 | 11.1 | 10.7
20 | 10.2 | 10.6 | 9.8
21 | 11.3 | 10.3 | 9.7
22 | 11.1 | 10 | 8.9
23 | 10.8 | 8.7 | 9.2
0 | 10.6 | 6.1 | 9.5
1 | 10.4 | 7 | 10
2 | 9.9 | 6.9 | 10.4
3 | 8.9 | 6.8 | 10
4 | 8.7 | 6.7 | 11.4
5 | 8.5 | 6.7 | 10.3
6 | 8.2 | 6.7 | 9.2
7 | 8.6 | 6.7 | 10
8 | 9 | 6.9 | 10.7
9 | 11.3 | 7.6 | 12
10 | 13.5 | 8.5 | 14.1
11 | 14.7 | 9.3 | 15.8
12 | 15.8 | 9.3 | 15.9
13 | 15.7 | 9.4 | 16.1
14 | 15.8 | 9.6 | 16.2
15 | 15.7 | 9.2 | 16.1
16 | 15.7 | 9.5 | 16.1
17 | 14.3 | 8.8 | 14.8
18 | 13.3 | 8.2 | 14.3
19 | 11.8 | 7.9 | 12.7
20 | 11.9 | 7.6 | 13
21 | 10.8 | 7.4 | 11.8
22 | 11.5 | 7.3 | 11.6
23 | 11.5 | 6.6 | 11.2
0 | 11.6 | 9 | 10.8
1 | 11 | 10.1 | 10.2
2 | 10.6 | 10 | 10
3 | 10.4 | 9.9 | 8.9
4 | 10.3 | 9.8 | 9.1
5 | 10.4 | 9.8 | 8.6
6 | 10.5 | 9.8 | 8.2
7 | 10.6 | 9.8 | 9.1
8 | 10.3 | 10.1 | 10.1
9 | 11.7 | 11 | 11.8
10 | 12.2 | 12.1 | 14.2
11 | 12.8 | 13.2 | 16.2
12 | 12.4 | 13.1 | 16.6
13 | 12.5 | 13.3 | 16.7
14 | 12.9 | 13.5 | 16.8
15 | 12.8 | 13.3 | 16.3
16 | 12.7 | 13.4 | 16.6
17 | 12.4 | 12.5 | 15.2
18 | 11.8 | 11.8 | 14
19 | 11.5 | 11.3 | 13
20 | 10.8 | 11 | 11.9
21 | 11.6 | 10.7 | 10.4
22 | 11.9 | 10.5 | 11.7
23 | 11.6 | 9.7 | 10.7
0 | 11.2 | 9.5 | 9.7
1 | 11.3 | 10.9 | 7.6
2 | 11.2 | 10.7 | 6.1
3 | 11.5 | 10.6 | 5.7
4 | 11.9 | 10.5 | 5.9
5 | 11.1 | 10.5 | 5.3
6 | 11.1 | 10.4 | 4.7
7 | 11 | 10.4 | 5.5
8 | 11.6 | 10.8 | 6.4
9 | 12 | 11.8 | 9.1
10 | 12.2 | 13.2 | 10.9
11 | 13 | 14.4 | 12.7
12 | 13 | 14.6 | 13.6
13 | 13.4 | 14.8 | 13.6
14 | 13.3 | 14.8 | 13.7
15 | 13 | 14.6 | 13.4
16 | 13 | 14.6 | 13
17 | 12.7 | 13.6 | 11.4
18 | 12.7 | 12.8 | 10.7
19 | 11.2 | 12.2 | 9.3
20 | 13.3 | 11.9 | 8.9
21 | 12.3 | 11.6 | 7.7
22 | 12.2 | 11.3 | 7.1
23 | 12.4 | 10.3 | 7.5
0 | 12.7 | 6 | 8
1 | 12.4 | 8.4 | 7.6
2 | 12.2 | 8.2 | 7.6
3 | 12.7 | 7.9 | 6.6
4 | 12.4 | 7.8 | 6.5
5 | 12 | 7.7 | 6.8
6 | 11.6 | 7.6 | 6.3
7 | 12.2 | 7.6 | 5.9
8 | 12.7 | 8.4 | 6.9
9 | 12.9 | 10.2 | 7.8
10 | 14.8 | 12.7 | 9.6
11 | 15.8 | 14.8 | 10.6
12 | 15.5 | 15.6 | 10.7
13 | 15.5 | 15.7 | 11.1
14 | 15.9 | 15.6 | 10.7
15 | 15.4 | 15.5 | 11.2
16 | 15.8 | 15.3 | 10.9
17 | 14.7 | 13.4 | 9.8
18 | 14.5 | 11.9 | 8.8
19 | 13.8 | 10.9 | 8.8
20 | 14 | 10.2 | 8.5
21 | 12.6 | 9.7 | 7.9
22 | 12.9 | 9.3 | 6.8
23 | 14.2 | 7.4 | 8.4
0 | 15.5 | 5.2 | 10.1
1 | 15.7 | 8.1 | 10.3
2 | 15.7 | 7.8 | 10.4
3 | 15.7 | 7.5 | 11.1
4 | 15.5 | 7.4 | 10.8
5 | 15.8 | 7.3 | 10.8
6 | 16 | 7.2 | 10.5
7 | 17.6 | 7.2 | 10.1
8 | 15.8 | 8 | 10.5
9 | 15.9 | 10.1 | 10.8
10 | 17.7 | 13 | 12.2
11 | 18.1 | 15.5 | 13.1
12 | 17.9 | 16.4 | 13.3
13 | 17.9 | 16.1 | 13.3
14 | 18.1 | 16.4 | 13.4
15 | 18.2 | 16.3 | 13
16 | 18.1 | 16 | 13.3
17 | 18.1 | 13.9 | 12.8
18 | 17.2 | 12.1 | 12.9
19 | 16.9 | 10.9 | 11.8
20 | 16.4 | 10.2 | 11.9
21 | 16.6 | 9.6 | 10.7
22 | 15.9 | 9.1 | 11.2
23 | 16.3 | 6.9 | 11.2
0 | 16.7 | 4.9 | 11.1
1 | 16.3 | 7.4 | 9.8
2 | 15.9 | 7.2 | 8.8
3 | 15.6 | 6.9 | 8.8
4 | 15.9 | 6.8 | 7.6
5 | 15.7 | 6.7 | 7.2
6 | 15.5 | 6.6 | 6.8
7 | 16.5 | 6.6 | 7.6
8 | 17.5 | 7.3 | 8.4
9 | 18.5 | 9.3 | 9.9
10 | 18.8 | 11.8 | 12.8
11 | 21 | 14 | 14.5
12 | 20.9 | 14.6 | 15.3
13 | 20.7 | 14.7 | 15
14 | 20.9 | 14.8 | 15.4
15 | 21 | 14.6 | 15.1
16 | 20.7 | 14.5 | 15.1
17 | 19.9 | 12.6 | 13.5
18 | 19 | 11 | 12.6
19 | 19.1 | 9.9 | 10.8
20 | 17.6 | 9.3 | 10.4
21 | 17.9 | 8.7 | 10.5
22 | 16.9 | 8.3 | 9.2
23 | 16.9 | 6.4 | 10.6
0 | 16.8 | 8.8 | 12
1 | 14.4 | 9.8 | 12.5
2 | 13.3 | 9.7 | 12.8
3 | 12.5 | 9.6 | 13.1
4 | 11.8 | 9.5 | 12.5
5 | 12.7 | 9.5 | 13.2
6 | 12.1 | 9.4 | 12.7
7 | 11.7 | 9.4 | 12
8 | 12.4 | 9.7 | 13.2
9 | 13.3 | 10.5 | 14.2
10 | 15.6 | 11.5 | 15.5
11 | 16.1 | 12.3 | 16.4
12 | 16.3 | 12.5 | 17.1
13 | 16.1 | 12.2 | 17.1
14 | 15.9 | 12.6 | 17
15 | 16.6 | 12.3 | 17
16 | 16 | 12.5 | 17
17 | 15.6 | 11.8 | 16
18 | 13.8 | 11.1 | 15.8
19 | 14.7 | 10.7 | 14.1
20 | 13.9 | 10.5 | 14.5
21 | 12.5 | 10.3 | 14.2
22 | 12.3 | 10.1 | 14.2
23 | 11.9 | 10 | 11.7
0 | 11.5 | 9.9 | 9.1
1 | 11 | 9.7 | 6.6
2 | 10.6 | 9.6 | 4.1
3 | 10.2 | 9.4 | 3.1
4 | 10.8 | 9.3 | 2.7
5 | 10.1 | 9.2 | 2.1
6 | 9.4 | 9.2 | 1.4
7 | 8.6 | 9.1 | 2.1
8 | 9.8 | 9.2 | 2.8
9 | 11 | 10 | 4.1
10 | 13.8 | 11.4 | 5.8
11 | 16.2 | 12.8 | 8.2
12 | 17 | 12.8 | 9.2
13 | 17.3 | 13 | 9.2
14 | 17.4 | 13.3 | 9.4
15 | 17.1 | 13.3 | 9.3
16 | 16.8 | 12.8 | 9.1
17 | 15.9 | 11.8 | 7.5
18 | 13.9 | 11.1 | 6.1
19 | 13.3 | 10.7 | 5.3
20 | 11.8 | 10.4 | 5.9
21 | 12.6 | 10.1 | 4.4
22 | 12.4 | 9.9 | 3.7
23 | 12.3 | 8.9 | 5
0 | 12.1 | 8.7 | 6.3
1 | 11.9 | 10.5 | 6.8
2 | 11.5 | 10.4 | 6.6
3 | 11.2 | 10.2 | 6.3
4 | 10.5 | 10.1 | 6.5
5 | 9.7 | 10 | 6.5
6 | 10.3 | 9.9 | 6.5
7 | 10.9 | 9.8 | 6.6
8 | 10.9 | 10 | 6.5
9 | 12.8 | 10.9 | 7.4
10 | 14.9 | 12.6 | 7.7
11 | 17.6 | 14.2 | 8.3
12 | 17.7 | 14.7 | 8.4
13 | 17.6 | 14.6 | 8.5
14 | 18 | 14.8 | 8.2
15 | 17.7 | 14.7 | 8.4
16 | 17.2 | 14.2 | 8
17 | 15.7 | 13 | 8.2
18 | 15 | 12.2 | 7.5
19 | 14.3 | 11.7 | 7.2
20 | 13.5 | 11.4 | 7.3
21 | 13.1 | 11 | 7.6
22 | 13.2 | 10.8 | 7.9
23 | 12.6 | 9.6 | 7.7
0 | 12.1 | 7 | 7.6
1 | 10.9 | 9.7 | 8.3
2 | 10.6 | 9.5 | 8.6
3 | 8.3 | 9.3 | 8.4
4 | 7.8 | 9 | 9.4
5 | 7.3 | 8.9 | 9.1
6 | 7.7 | 8.8 | 8.4
7 | 8.2 | 8.7 | 7.6
8 | 8.9 | 8.9 | 8.7
9 | 10.3 | 10.2 | 9.6
10 | 13 | 12.6 | 10.7
11 | 15.9 | 14.8 | 12.3
12 | 16.5 | 15.4 | 12.9
13 | 16.4 | 15.7 | 13
14 | 16.6 | 15.6 | 13.1
15 | 16.5 | 15.4 | 13
16 | 16.2 | 14.8 | 12.8
17 | 14.1 | 13.1 | 11.7
18 | 13.3 | 12 | 11.2
19 | 13.6 | 11.4 | 10.7
20 | 11.5 | 10.9 | 10.2
21 | 10.9 | 10.4 | 10.2
22 | 11 | 10 | 10.1
23 | 10.5 | 8.4 | 9.1
0 | 10 | 10.3 | 8.1
1 | 9.2 | 11.1 | 6.4
2 | 8.6 | 11 | 5.1
3 | 8.5 | 11 | 5
4 | 8.4 | 10.9 | 4.9
5 | 8.3 | 10.9 | 5
6 | 8.5 | 10.8 | 4.7
7 | 8.8 | 10.8 | 4.2
8 | 9.6 | 10.9 | 3.8
9 | 8.3 | 11.2 | 5.6
10 | 9.3 | 11.9 | 7.4
11 | 9.5 | 12.5 | 8.5
12 | 9.4 | 12.5 | 9.1
13 | 9.2 | 12.3 | 8.9
14 | 9.7 | 12.8 | 9.3
15 | 9.6 | 12.5 | 9
16 | 9.2 | 12.5 | 8.9
17 | 8.3 | 12.1 | 7.9
18 | 8.9 | 11.7 | 7.6
19 | 9 | 11.6 | 6.3
20 | 8.7 | 11.4 | 6.3
21 | 8.6 | 11.3 | 5.3
22 | 9.1 | 11.2 | 5.6
23 | 9.2 | 10.7 | 5.5
0 | 9.3 | 7.4 | 5.4
1 | 9.4 | 8 | 5.7
2 | 9.9 | 8 | 5.7
3 | 8.9 | 7.9 | 5.3
4 | 9.1 | 7.8 | 5.8
5 | 8.9 | 7.8 | 5
6 | 8.6 | 7.8 | 4.1
7 | 9.5 | 7.8 | 4.7
8 | 10.5 | 7.8 | 5.1
9 | 9.9 | 8.1 | 6.2
10 | 10.2 | 8.7 | 7.6
11 | 10.5 | 9.2 | 9.8
12 | 10.5 | 9.1 | 10.5
13 | 10.4 | 9.3 | 10.7
14 | 10.6 | 9.4 | 10.4
15 | 10.5 | 9.3 | 10.6
16 | 10.9 | 9.2 | 10.4
17 | 10 | 8.8 | 9.1
18 | 10.5 | 8.6 | 8.6
19 | 9.3 | 8.4 | 7.9
20 | 9 | 8.3 | 7.3
21 | 8.8 | 8.2 | 7.2
22 | 8.6 | 8.1 | 6.6
23 | 8.6 | 7.7 | 7.4
0 | 8 | 5.7 | 8.3
1 | 6.3 | 7.8 | 9.3
2 | 5.3 | 7.7 | 9.7
3 | 4.5 | 7.5 | 9.8
4 | 3.7 | 7.3 | 9.8
5 | 4.1 | 7.2 | 9.1
6 | 4.5 | 7.1 | 8.3
7 | 4.9 | 7 | 9.2
8 | 4.6 | 7.2 | 9.8
9 | 7 | 8.2 | 9.8
10 | 8.3 | 10 | 12.8
11 | 10.9 | 11.7 | 13.1
12 | 11 | 12.1 | 14.1
13 | 11 | 12.1 | 14.3
14 | 11.1 | 12.4 | 14.4
15 | 11 | 12.4 | 14.3
16 | 10.7 | 11.7 | 14.2
17 | 8.7 | 10.4 | 13
18 | 7.5 | 9.6 | 12.6
19 | 7 | 9.1 | 12.3
20 | 6.9 | 8.7 | 10.9
21 | 7.7 | 8.3 | 10.9
22 | 7.1 | 8.1 | 10.5
23 | 6.7 | 6.8 | 10.2
0 | 6.3 | 3 | 9.9
1 | 6.1 | 5.4 | 9.6
2 | 5.7 | 5.2 | 9.3
3 | 4.5 | 5 | 9
4 | 3.2 | 4.8 | 10.2
5 | 4.2 | 4.7 | 8.8
6 | 5 | 4.6 | 8.3
7 | 4.7 | 4.5 | 7.7
8 | 4.9 | 4.7 | 9.1
9 | 6.5 | 5.8 | 10.6
10 | 9.8 | 7.9 | 11.8
11 | 12.5 | 9.8 | 14
12 | 13.3 | 10.7 | 14.4
13 | 13.4 | 10.5 | 14.8
14 | 13.3 | 10.6 | 14.4
15 | 13.3 | 10.5 | 14.6
16 | 12 | 9.8 | 14.4
17 | 11.1 | 8.4 | 13.1
18 | 9.6 | 7.4 | 12.3
19 | 9.2 | 6.8 | 10.8
20 | 8.5 | 6.4 | 10.9
21 | 7.1 | 5.9 | 11.1
22 | 7.7 | 5.6 | 9.6
23 | 7.3 | 4.2 | 9.6
0 | 6.9 | -0.3 | 9.6
1 | 7 | 3 | 9.5
2 | 6.9 | 2.8 | 9.2
3 | 6.1 | 2.4 | 8.9
4 | 7.4 | 2.1 | 8.1
5 | 6.1 | 2 | 7.1
6 | 4.7 | 1.9 | 7.8
7 | 5.6 | 1.7 | 8.4
8 | 6.4 | 2 | 8.9
9 | 8.7 | 3.6 | 10.2
10 | 12 | 6.4 | 12.3
11 | 13.8 | 9.2 | 14.7
12 | 14.7 | 10.3 | 15.6
13 | 14.7 | 10.3 | 15.7
14 | 14.8 | 10.2 | 15.5
15 | 14.6 | 10.4 | 15.6
16 | 14.5 | 9.2 | 15
17 | 12.5 | 7.1 | 13.4
18 | 10.5 | 5.8 | 12.7
19 | 10.9 | 5 | 11.9
20 | 9.9 | 4.4 | 11.3
21 | 8.8 | 3.8 | 10.6
22 | 7.9 | 3.4 | 10.1
23 | 7.6 | 1.3 | 9.7
0 | 7.3 | -2.6 | 9.2
1 | 7.1 | 0.6 | 8.7
2 | 6.3 | 0.4 | 8.5
3 | 7.1 | 0.1 | 8.1
4 | 7.7 | -0.2 | 6.9
5 | 7.7 | -0.3 | 5.7
6 | 8.1 | -0.4 | 6.5
7 | 7.9 | -0.6 | 7.3
8 | 8.5 | -0.4 | 7.5
9 | 9.5 | 1.3 | 8.5
10 | 11.5 | 4 | 11.6
11 | 14.5 | 6.7 | 13.5
12 | 14.7 | 7.7 | 15.2
13 | 14.8 | 7.6 | 15.3
14 | 14.6 | 7.7 | 15.2
15 | 14.7 | 7.6 | 15.2
16 | 14.4 | 6.7 | 14.6
17 | 13.2 | 4.7 | 13.1
18 | 12.1 | 3.4 | 11.4
19 | 11 | 2.6 | 10.8
20 | 10.5 | 2 | 10.2
21 | 8.9 | 1.4 | 9.5
22 | 9.8 | 1 | 9.5
23 | 10.5 | -1 | 9.2
0 | 11.2 | 0.3 | 8.8
1 | 11.5 | 3.4 | 8.8
2 | 11.7 | 3.2 | 8.8
3 | 11.5 | 2.9 | 8.5
4 | 11.4 | 2.6 | 8.2
5 | 11.3 | 2.5 | 8.4
6 | 11.2 | 2.4 | 8.6
7 | 11.5 | 2.2 | 8.5
8 | 11.8 | 2.5 | 8.8
9 | 12.4 | 4 | 9
10 | 13.1 | 6.7 | 9.6
11 | 13.1 | 9.2 | 10.2
12 | 13.4 | 10 | 10.2
13 | 13.2 | 10.3 | 10.3
14 | 13 | 10.2 | 9.8
15 | 13 | 10.2 | 10.2
16 | 13.3 | 9.2 | 9.9
17 | 13.3 | 7.3 | 9.6
18 | 12.6 | 6.1 | 9.4
19 | 11.8 | 5.3 | 9.5
20 | 12.2 | 4.7 | 8.9
21 | 12.3 | 4.2 | 8.7
22 | 12.6 | 3.8 | 9
23 | 12 | 1.9 | 8.3
0 | 11.5 | -0.8 | 7.6
1 | 10.8 | 1.6 | 6.3
2 | 9.8 | 1.5 | 5.1
3 | 10.9 | 1.2 | 5.7
4 | 9.7 | 1 | 6.3
5 | 9.3 | 0.9 | 5.7
6 | 8.9 | 0.8 | 5.3
7 | 9.6 | 0.7 | 6.5
8 | 10.2 | 0.9 | 5.4
9 | 11.1 | 2.1 | 6.3
10 | 12.8 | 4.1 | 7.2
11 | 13.8 | 6.1 | 8.7
12 | 14.3 | 6.6 | 8.8
13 | 14.4 | 6.7 | 8.9
14 | 14.2 | 6.8 | 8.7
15 | 14.2 | 6.6 | 8.8
16 | 14.3 | 6.1 | 8.6
17 | 13.4 | 4.6 | 7.9
18 | 12 | 3.6 | 7.2
19 | 12.1 | 3.1 | 6.8
20 | 11.4 | 2.6 | 6.8
21 | 10.7 | 2.2 | 7
22 | 10.8 | 1.9 | 6.7
23 | 9.7 | 0.4 | 6.2
0 | 8.7 | 2 | 5.7
1 | 7.4 | 4.5 | 5.4
2 | 6.3 | 4.3 | 5.2
3 | 6.5 | 4.1 | 4.4
4 | 6 | 3.8 | 3.8
5 | 6.2 | 3.7 | 3.2
6 | 5.5 | 3.7 | 3.7
7 | 4.7 | 3.5 | 4.1
8 | 6.3 | 3.7 | 4.3
9 | 7.9 | 5 | 6.3
10 | 10.6 | 7.1 | 8.4
11 | 12.2 | 9.2 | 9.4
12 | 13.1 | 10.1 | 10
13 | 13.7 | 10 | 10.1
14 | 13.8 | 10 | 10.2
15 | 13.5 | 9.7 | 10.1
16 | 13.7 | 9.2 | 10.1
17 | 11.7 | 7.7 | 8.1
18 | 10.2 | 6.6 | 7.6
19 | 10 | 6 | 6.8
20 | 9 | 5.6 | 6.7
21 | 8.4 | 5.1 | 5.6
22 | 7.7 | 4.8 | 5.3
23 | 7.6 | 3.2 | 6.7
0 | 7.5 | 5 | 8.1
1 | 7.1 | 6.1 | 9.1
2 | 6.6 | 6 | 9.8
3 | 6 | 5.9 | 10.3
4 | 6.2 | 5.8 | 9.3
5 | 6.8 | 5.8 | 8.1
6 | 5.7 | 5.7 | 8.8
7 | 4.7 | 5.7 | 9.2
8 | 6.7 | 5.8 | 9.6
9 | 8.7 | 6.3 | 10.6
10 | 11.1 | 7.1 | 12.4
11 | 13.5 | 8 | 14.5
12 | 14.4 | 7.8 | 14.8
13 | 14.2 | 7.8 | 14.8
14 | 14.5 | 8.3 | 14.9
15 | 14.4 | 7.8 | 14.8
16 | 13.6 | 8 | 14.8
17 | 12.1 | 7.4 | 13.5
18 | 10.9 | 6.9 | 12.7
19 | 10.1 | 6.7 | 11.3
20 | 9.2 | 6.5 | 11.4
21 | 8.2 | 6.3 | 11.3
22 | 9.2 | 6.2 | 10.5
23 | 8.4 | 5.5 | 9.8
0 | 7.6 | 6.7 | 9
1 | 7.8 | 9 | 7.5
2 | 7.7 | 8.9 | 6.2
3 | 8.4 | 8.6 | 6.7
4 | 7.6 | 8.4 | 6.3
5 | 8 | 8.3 | 5.6
6 | 7.5 | 8.3 | 5.1
7 | 6.7 | 8.1 | 6.1
8 | 7.6 | 8.3 | 7.1
9 | 8.3 | 9.5 | 7.2
10 | 10.4 | 11.5 | 10.3
11 | 11.8 | 13.4 | 11.5
12 | 11.9 | 14.1 | 12
13 | 11.9 | 14 | 12.3
14 | 11.9 | 14.1 | 12.5
15 | 11.8 | 14.2 | 12.1
16 | 11.3 | 13.4 | 12.3
17 | 10.1 | 12 | 11.3
18 | 9.4 | 11 | 9.5
19 | 9.6 | 10.5 | 9
20 | 9.7 | 10 | 8.2
21 | 9.1 | 9.6 | 7.7
22 | 8.8 | 9.3 | 8.2
23 | 8 | 7.9 | 8
0 | 7.3 | 3.3 | 7.7
1 | 6.2 | 5.7 | 7.8
2 | 5.3 | 5.5 | 7.9
3 | 5.1 | 5.3 | 8.2
4 | 4.6 | 5.1 | 7.4
5 | 3.7 | 5 | 6.7
6 | 2.8 | 4.9 | 7.1
7 | 4.1 | 4.7 | 7.6
8 | 5.3 | 5 | 7.5
9 | 6 | 6.2 | 8.2
10 | 9.7 | 8.3 | 9.2
11 | 13 | 10.4 | 11
12 | 14 | 11.2 | 11.2
13 | 14.1 | 11.2 | 11.3
14 | 13.9 | 11.1 | 11.6
15 | 14 | 10.8 | 11.4
16 | 13.5 | 10.4 | 11.4
17 | 12 | 8.8 | 10.9
18 | 10.3 | 7.8 | 9.4
19 | 8.7 | 7.2 | 9.7
20 | 8 | 6.8 | 8.7
21 | 7.6 | 6.3 | 8.7
22 | 6.7 | 6 | 8.9
23 | 6.4 | 4.5 | 7.5
0 | 6.1 | 4 | 6
1 | 5.4 | 6.1 | 4
2 | 5 | 6 | 2.8
3 | 4.4 | 5.9 | 1.8
4 | 5 | 5.7 | 1.6
5 | 4.3 | 5.6 | 1.9
6 | 3.6 | 5.6 | 1.3
7 | 4.4 | 5.6 | 0.7
8 | 5.1 | 5.6 | 1.5
9 | 5.4 | 6.3 | 2.3
10 | 7.1 | 7.9 | 4.9
11 | 8.9 | 9.8 | 6
12 | 9.7 | 10.8 | 7.4
13 | 9.8 | 10.6 | 7
14 | 9.7 | 10.9 | 7.4
15 | 9.5 | 10.8 | 7.2
16 | 9.4 | 9.9 | 6.8
17 | 8.2 | 8.6 | 6.2
18 | 7.5 | 7.9 | 4.6
19 | 7 | 7.6 | 5.7
20 | 6.7 | 7.2 | 3.2
21 | 6.1 | 6.8 | 3.4
22 | 5.8 | 6.6 | 2.7
23 | 5.8 | 5 | 3.8
0 | 5.8 | 5.7 | 4.9
1 | 6 | 6.1 | 5.1
2 | 6.2 | 6 | 5.2
3 | 6.5 | 6 | 6
4 | 5.6 | 6 | 5.5
5 | 6.4 | 6 | 4.9
6 | 5.8 | 6 | 5.3
7 | 5.2 | 6 | 5.7
8 | 5.9 | 6 | 5.6
9 | 6.5 | 6.1 | 6.1
10 | 8.3 | 6.3 | 6.5
11 | 9.1 | 6.6 | 7.5
12 | 9.3 | 6.3 | 7.2
13 | 9.5 | 6.3 | 7.2
14 | 9.6 | 6.8 | 7.6
15 | 9.5 | 6.6 | 7.5
16 | 9.1 | 6.6 | 7.5
17 | 7.7 | 6.4 | 7
18 | 7.7 | 6.3 | 6.3
19 | 8.1 | 6.3 | 6.7
20 | 6.7 | 6.2 | 6.5
21 | 6.9 | 6.2 | 5.5
22 | 7.1 | 6.1 | 5.7
23 | 6.5 | 5.9 | 5.4
0 | 6 | 3.8 | 5.1
1 | 4.6 | 6.5 | 4.8
2 | 3.7 | 6.4 | 4.8
3 | 2.3 | 6.2 | 4.4
4 | 2.9 | 6 | 4
5 | 2.6 | 5.9 | 4.4
6 | 2.3 | 5.9 | 4.8
7 | 2 | 5.8 | 4.4
8 | 1.8 | 5.8 | 4.5
9 | 2.9 | 6.7 | 4.3
10 | 4.1 | 8.6 | 4.7
11 | 6.9 | 11 | 6.3
12 | 6.9 | 12.2 | 6.3
13 | 7 | 12.4 | 6.8
14 | 7.1 | 12.4 | 6.7
15 | 6.7 | 12.4 | 6.7
16 | 6.6 | 11.1 | 6.7
17 | 5.4 | 9.5 | 6.4
18 | 5.6 | 8.7 | 5.6
19 | 4.8 | 8.3 | 5.1
20 | 4 | 7.8 | 5.9
21 | 4 | 7.3 | 5
22 | 3.8 | 7 | 5.3
23 | 4.6 | 5.2 | 5.2
0 | 5.3 | 5.6 | 5.1
1 | 5.6 | 6 | 4.9
2 | 5.8 | 6 | 4.7
3 | 5.6 | 5.9 | 5.3
4 | 5.7 | 5.9 | 4.4
5 | 5.5 | 5.9 | 4.8
6 | 5.5 | 5.9 | 3.8
7 | 5.5 | 5.9 | 2.8
8 | 5.4 | 5.9 | 3.9
9 | 5.3 | 6 | 4.9
10 | 5.4 | 6.3 | 6.2
11 | 5.5 | 6.7 | 9
12 | 5.9 | 6.4 | 10.2
13 | 5.8 | 6.6 | 10.2
14 | 5.7 | 6.9 | 10.3
15 | 5.9 | 6.3 | 10.1
16 | 5.4 | 6.7 | 10.2
17 | 5.5 | 6.5 | 8
18 | 5.5 | 6.3 | 8.1
19 | 5.8 | 6.3 | 6.6
20 | 5.6 | 6.2 | 7.2
21 | 5.5 | 6.1 | 5.4
22 | 5.5 | 6.1 | 5.7
23 | 5.5 | 5.8 | 5
0 | 5.5 | 3 | 4.3
1 | 5.5 | 4.3 | 3.8
2 | 5.6 | 4.3 | 3.2
3 | 5.3 | 4.2 | 3.7
4 | 5.1 | 4.1 | 2.8
5 | 5.2 | 4 | 2.8
6 | 5.8 | 4 | 2.6
7 | 5.4 | 4 | 1.9
8 | 5 | 4 | 1.1
9 | 5.4 | 4.4 | 3.7
10 | 5.9 | 5.4 | 6.2
11 | 6 | 6.5 | 8.9
12 | 5.8 | 7.1 | 10.1
13 | 6.3 | 6.7 | 10.3
14 | 6.1 | 7.1 | 10.4
15 | 5.8 | 6.9 | 10.3
16 | 6 | 6.5 | 10.1
17 | 5.9 | 5.8 | 8.1
18 | 5.6 | 5.4 | 7.1
19 | 5.6 | 5.2 | 6.7
20 | 5.4 | 4.9 | 6
21 | 5.5 | 4.7 | 5.4
22 | 5.9 | 4.6 | 4.5
23 | 5.8 | 3.7 | 4.3
0 | 5.8 | 6.3 | 4.1
1 | 5.6 | 8.1 | 4.6
2 | 5.3 | 8 | 4.8
3 | 5.3 | 7.9 | 3.8
4 | 4.8 | 7.8 | 2.7
5 | 4.2 | 7.7 | 3.6
6 | 3.6 | 7.7 | 4.4
7 | 4.5 | 7.6 | 4.3
8 | 5.3 | 7.6 | 4
9 | 5.9 | 8.2 | 5.6
10 | 8.4 | 9.6 | 6.5
11 | 9.7 | 11.3 | 8.1
12 | 10.8 | 12.1 | 9.8
13 | 10.6 | 11.8 | 9.8
14 | 10.9 | 12.2 | 9.9
15 | 10.8 | 12.2 | 9.7
16 | 10.2 | 11.4 | 9.4
17 | 8.9 | 10.3 | 8.4
18 | 8.7 | 9.7 | 6.7
19 | 7.4 | 9.4 | 6.6
20 | 7.3 | 9 | 6.8
21 | 7.1 | 8.7 | 5.1
22 | 6.2 | 8.5 | 6.2
23 | 6.4 | 7.2 | 6.3
0 | 6.6 | 4.6 | 6.4
1 | 6.9 | 8.1 | 6.7
2 | 7.2 | 8 | 6.9
3 | 7.3 | 7.7 | 6.7
4 | 7 | 7.4 | 6.4
5 | 6.6 | 7.3 | 6.9
6 | 6.8 | 7.3 | 7.3
7 | 6.9 | 7.2 | 7.2
8 | 7 | 7.2 | 7.5
9 | 6.9 | 8.3 | 7.3
10 | 7.2 | 10.9 | 7.8
11 | 8 | 14 | 8.4
12 | 7.9 | 15.6 | 8.1
13 | 8.2 | 15.9 | 8.5
14 | 8.1 | 15.7 | 8.4
15 | 8.2 | 15.5 | 8.1
16 | 8.1 | 14.1 | 8.1
17 | 7.6 | 12.1 | 8.1
18 | 7.7 | 11 | 7.6
19 | 7.5 | 10.4 | 7.5
20 | 7.4 | 9.8 | 7
21 | 6.8 | 9.1 | 7.3
22 | 6.8 | 8.8 | 7
23 | 7.4 | 6.4 | 7.3
0 | 7.9 | 4.8 | 7.5
1 | 7.8 | 7.7 | 7.7
2 | 7.6 | 7.6 | 7.6
3 | 7.3 | 7.4 | 7.5
4 | 7.5 | 7.1 | 7.7
5 | 7.1 | 7 | 7.9
6 | 6.1 | 7 | 7.8
7 | 5.2 | 6.9 | 7.6
8 | 7.5 | 7 | 7.9
9 | 9.7 | 7.9 | 7.8
10 | 11.1 | 10 | 7.8
11 | 13.9 | 12.6 | 7.9
12 | 15.1 | 14.1 | 8
13 | 15 | 14 | 7.5
14 | 15.2 | 14 | 7.6
15 | 15.1 | 14.1 | 7.9
16 | 14.7 | 12.7 | 7.6
17 | 12.1 | 11 | 8
18 | 10.9 | 10.1 | 7.8
19 | 11.5 | 9.6 | 7.6
20 | 10.3 | 9.1 | 7.8
21 | 8.8 | 8.5 | 7.6
22 | 9.4 | 8.3 | 7.7
23 | 10.9 | 6.2 | 7.5
0 | 12.4 | 6.9 | 7
1 | 13.9 | 9.2 | 6.3
2 | 15.2 | 9 | 6
3 | 14.1 | 8.9 | 5
4 | 13.2 | 8.7 | 5.7
5 | 12.9 | 8.6 | 5
6 | 13.3 | 8.6 | 5.7
7 | 13 | 8.6 | 6.1
8 | 12.4 | 8.6 | 5.4
9 | 14.1 | 9.3 | 4.7
10 | 15.6 | 10.9 | 5.8
11 | 17.3 | 12.9 | 6.9
12 | 17.8 | 13.7 | 7.4
13 | 17.9 | 13.6 | 7.7
14 | 17.8 | 14 | 7.6
15 | 17.8 | 14 | 7.4
16 | 17.8 | 13 | 7.6
17 | 16.7 | 11.7 | 6.3
18 | 15.8 | 11 | 6
19 | 15.3 | 10.6 | 6.3
20 | 15.6 | 10.2 | 6.2
21 | 14.4 | 9.8 | 5.9
22 | 13.7 | 9.6 | 5.3
23 | 14 | 8 | 6.3
0 | 14.3 | 7 | 7.4
1 | 13.9 | 9 | 8.3
2 | 13.5 | 8.9 | 8.6
3 | 13.2 | 8.8 | 8.1
4 | 13 | 8.6 | 7.4
5 | 13.2 | 8.5 | 7.8
6 | 12.3 | 8.5 | 8
7 | 11.3 | 8.5 | 8.3
8 | 13.3 | 8.5 | 7.9
9 | 15.3 | 9.1 | 9.5
10 | 17.1 | 10.6 | 10.5
11 | 19 | 12.4 | 11.6
12 | 20.5 | 13.4 | 12.3
13 | 20.4 | 13.4 | 12.1
14 | 20.6 | 13.4 | 12.4
15 | 20.4 | 13.5 | 12.3
16 | 19.5 | 12.5 | 11.9
17 | 17.8 | 11.3 | 11.2
18 | 17.4 | 10.7 | 11.2
19 | 16.2 | 10.4 | 10
20 | 15.9 | 10 | 10.7
21 | 14.7 | 9.6 | 10
22 | 15 | 9.4 | 9.4
23 | 14.8 | 8 | 10
0 | 14.6 | 10.9 | 10.6
1 | 14.2 | 11.3 | 11.2
2 | 14.6 | 11.2 | 11.7
3 | 13.1 | 11.2 | 11.2
4 | 13.3 | 11.2 | 10.6
5 | 13.4 | 11.2 | 11.1
6 | 13.1 | 11.2 | 11.4
7 | 13.8 | 11.2 | 11.2
8 | 13.7 | 11.2 | 11
9 | 13.2 | 11.3 | 12.1
10 | 14.7 | 11.5 | 13
11 | 15.8 | 11.9 | 14.3
12 | 15.9 | 11.6 | 14.2
13 | 16.1 | 11.5 | 14.5
14 | 16.2 | 12 | 14.4
15 | 16.1 | 11.9 | 14.4
16 | 16.1 | 11.9 | 14.4
17 | 14.5 | 11.7 | 13.5
18 | 14.3 | 11.5 | 12.6
19 | 14.6 | 11.5 | 12.4
20 | 14.2 | 11.4 | 13
21 | 14.6 | 11.4 | 12.3
22 | 14.9 | 11.3 | 12.5
23 | 13.8 | 11.1 | 12.1
0 | 12.7 | 4.4 | 11.7
1 | 10.8 | 6.3 | 10.8
2 | 9.4 | 6.2 | 9.9
3 | 10.1 | 6.1 | 10.2
4 | 10.5 | 5.9 | 10.5
5 | 10.2 | 5.8 | 10
6 | 9.7 | 5.9 | 10.1
7 | 9.1 | 5.8 | 10.1
8 | 9.2 | 5.8 | 10.6
9 | 9.3 | 6.4 | 10.5
10 | 12.1 | 7.8 | 11.2
11 | 12.9 | 9.5 | 12.5
12 | 13 | 10.4 | 12.2
13 | 13.1 | 10.4 | 12.6
14 | 12.7 | 10.4 | 12.2
15 | 13 | 10.2 | 12.4
16 | 12.6 | 9.6 | 12.2
17 | 12.1 | 8.4 | 11.5
18 | 10.9 | 7.8 | 11.5
19 | 11.6 | 7.5 | 11.9
20 | 11.1 | 7.2 | 11.7
21 | 10.9 | 6.8 | 11.1
22 | 10 | 6.7 | 11.4
23 | 10 | 5.4 | 10.9
0 | 10.1 | 3.3 | 10.4
1 | 9.5 | 4.7 | 9.6
2 | 9.1 | 4.7 | 8.9
3 | 9.3 | 4.6 | 9
4 | 9.6 | 4.4 | 8.7
5 | 8.6 | 4.4 | 8.2
6 | 7.7 | 4.4 | 8.4
7 | 8.4 | 4.4 | 7.7
8 | 9.1 | 4.4 | 7
9 | 9.8 | 4.8 | 9.5
10 | 11.5 | 5.9 | 12
11 | 12.1 | 7.2 | 13.9
12 | 13.4 | 7.7 | 15.4
13 | 13.3 | 8 | 15.3
14 | 13.6 | 8 | 15.6
15 | 13.3 | 7.7 | 15.4
16 | 13.3 | 7.3 | 15
17 | 12.3 | 6.4 | 13.8
18 | 10.7 | 6 | 11.8
19 | 10.9 | 5.7 | 11.9
20 | 10.1 | 5.4 | 11.2
21 | 10.5 | 5.2 | 11
22 | 9.7 | 5 | 10.5
23 | 8.7 | 4 | 10.1
0 | 7.6 | 0.2 | 9.6
1 | 5.7 | 2.3 | 9.6
2 | 4.8 | 2.2 | 9.9
3 | 4.3 | 2.1 | 9.6
4 | 4.1 | 1.9 | 9
5 | 5.2 | 1.8 | 8.7
6 | 4.6 | 1.8 | 8.4
7 | 3.4 | 1.8 | 8.7
8 | 2.4 | 1.8 | 8.9
9 | 5 | 2.5 | 9.8
10 | 7.7 | 4 | 10.5
11 | 10.4 | 5.9 | 11.4
12 | 11.1 | 7 | 11.4
13 | 11.4 | 6.6 | 11.4
14 | 11.5 | 6.9 | 11.9
15 | 11.4 | 6.9 | 11.6
16 | 10.9 | 6 | 11.6
17 | 9.1 | 4.7 | 10.9
18 | 7.3 | 4.1 | 9.9
19 | 7.4 | 3.7 | 10.8
20 | 7.2 | 3.3 | 9.8
21 | 5.4 | 2.9 | 9.6
22 | 5.3 | 2.7 | 8.8
23 | 4.8 | 1.3 | 8.4
0 | 4.3 | -0.8 | 7.9
1 | 3.8 | 1.3 | 6.1
2 | 3.7 | 1.2 | 4.6
3 | 2 | 1.1 | 3.8
4 | 2.2 | 0.9 | 3.1
5 | 1.2 | 0.8 | 4
6 | 1.9 | 0.8 | 4.9
7 | 0.3 | 0.7 | 4.6
8 | -1.3 | 0.8 | 4.2
9 | 2.8 | 1.4 | 5.9
10 | 6.9 | 3 | 7.8
11 | 10.2 | 4.9 | 9.8
12 | 12.9 | 6 | 11.1
13 | 13 | 5.6 | 11.1
14 | 13.1 | 5.9 | 11.2
15 | 13 | 5.8 | 11.1
16 | 12.3 | 5 | 10.8
17 | 9.7 | 3.7 | 9.2
18 | 7.1 | 3.1 | 8.6
19 | 5.7 | 2.7 | 7.6
20 | 5.8 | 2.3 | 7.2
21 | 4.8 | 1.9 | 5.7
22 | 4.7 | 1.7 | 5.3
23 | 5.8 | 3.2 | 4.7
0 | 7 | 4.7 | 4.2
1 | 8.1 | 6.2 | 3.6
2 | 9.3 | 7.7 | 3
3 | 8.5 | 7.5 | 2.9
4 | 8.3 | 7.4 | 3.2
5 | 8.3 | 7.3 | 3.3
6 | 8.1 | 7.2 | 2.7
7 | 7.7 | 7.2 | 2.2
8 | 7.4 | 7.1 | 2.7
9 | 8.7 | 7.5 | 3.2
10 | 10.1 | 8.7 | 4.8
11 | 11.2 | 10.5 | 6.1
12 | 12.5 | 12.2 | 5.8
13 | 12.8 | 12.1 | 5.9
14 | 12.7 | 11.8 | 6.2
15 | 12.7 | 12.1 | 5.8
16 | 11.8 | 11 | 5.4
17 | 11.1 | 9.9 | 4.7
18 | 10.5 | 9.3 | 4.7
19 | 10.7 | 9.1 | 4.6
20 | 9.7 | 8.8 | 4.1
21 | 9.4 | 8.5 | 3.9
22 | 10.1 | 8.3 | 3.3
23 | 10.1 | 6.8 | 3
0 | 10 | 6 | 2.7
1 | 10.5 | 6.9 | 1.2
2 | 10.2 | 6.8 | -0.1
3 | 10.3 | 6.8 | -0.1
4 | 10 | 6.7 | -0.1
5 | 10.1 | 6.6 | -0.4
6 | 10.1 | 6.6 | -0.5
7 | 9.3 | 6.6 | -0.9
8 | 8.2 | 6.6 | -1.4
9 | 10.8 | 6.7 | -0.1
10 | 13.1 | 7.2 | 1.2
11 | 15.1 | 8 | 3.5
12 | 17.2 | 8.7 | 4.6
13 | 17.3 | 8.6 | 4.5
14 | 17.1 | 8.4 | 4.7
15 | 17.2 | 8.4 | 4.3
16 | 16.4 | 8.2 | 4.5
17 | 15.1 | 7.7 | 3.5
18 | 14.5 | 7.5 | 2.7
19 | 13.3 | 7.4 | 2.3
20 | 13.3 | 7.3 | 1.6
21 | 12.5 | 7.1 | 1.1
22 | 11.9 | 7.1 | 0.9
23 | 11 | 6.5 | 0.8
0 | 10.2 | 7.1 | 0.6
1 | 8.8 | 8 | 0.2
2 | 7.9 | 7.9 | -0.2
3 | 6.9 | 7.9 | -0.3
4 | 7.7 | 7.8 | -0.8
5 | 8.5 | 7.8 | -0.7
6 | 7.4 | 7.7 | -1
7 | 7.7 | 7.7 | -1.8
8 | 7.7 | 7.7 | -2.6
9 | 7.6 | 7.9 | -0.3
10 | 9.1 | 8.3 | 1.9
11 | 10.9 | 9 | 3.9
12 | 11.1 | 9.7 | 6.1
13 | 11.2 | 9.7 | 6.3
14 | 11.5 | 9.2 | 6.4
15 | 11.2 | 9.3 | 6.3
16 | 11.1 | 9.2 | 5.6
17 | 10 | 8.8 | 4.1
18 | 9.8 | 8.6 | 3.9
19 | 9.5 | 8.5 | 2.5
20 | 9.2 | 8.4 | 2.1
21 | 8.9 | 8.2 | 1.7
22 | 9 | 8.2 | 1.8
23 | 8.5 | 7.6 | 0.9
0 | 8 | 6.2 | 0
1 | 7.4 | 6.9 | -0.1
2 | 7 | 6.8 | -0.4
3 | 6.2 | 6.8 | -0.7
4 | 7 | 6.7 | -1.1
5 | 6.5 | 6.7 | -1.1
6 | 7.1 | 6.7 | -1.3
7 | 6.3 | 6.7 | -2.1
8 | 5.4 | 6.6 | -3
9 | 6.5 | 6.8 | -1.1
10 | 7.6 | 7.1 | 0.7
11 | 10.2 | 7.7 | 4
12 | 10.5 | 8.3 | 6
13 | 10.2 | 8.3 | 5.8
14 | 10.6 | 8.2 | 6.1
15 | 10.5 | 8 | 5.9
16 | 10.5 | 7.9 | 5.9
17 | 8.8 | 7.5 | 3.8
18 | 8.5 | 7.3 | 2.2
19 | 8 | 7.3 | 2
20 | 8.1 | 7.2 | 1.9
21 | 8.1 | 7.1 | 1.3
22 | 6.9 | 7 | 0.6
23 | 7.1 | 6.6 | 1.6
0 | 7.3 | 9.1 | 2.6
1 | 7.9 | 10.1 | 4.4
2 | 8.3 | 10 | 5.3
3 | 8.4 | 9.9 | 5.2
4 | 7.8 | 9.8 | 5.5
5 | 7.1 | 9.8 | 4.8
6 | 7.7 | 9.8 | 4.5
7 | 8.1 | 9.8 | 3.6
8 | 8 | 9.7 | 2.4
9 | 8.7 | 9.9 | 5.2
10 | 9.1 | 10.4 | 7.6
11 | 10.3 | 11.1 | 10.5
12 | 11.3 | 11.9 | 12.6
13 | 11.4 | 11.8 | 12.7
14 | 11.2 | 11.8 | 12.6
15 | 11.1 | 11.7 | 12.6
16 | 11.3 | 11.4 | 11.8
17 | 9.7 | 10.9 | 9.5
18 | 9.8 | 10.7 | 9.4
19 | 9.9 | 10.5 | 8.5
20 | 9.4 | 10.4 | 8.2
21 | 8.9 | 10.3 | 7.7
22 | 8.9 | 10.2 | 7.3
23 | 9.1 | 9.6 | 6.8
0 | 9.3 | 6.8 | 6.2
1 | 9.5 | 9.1 | 6.2
2 | 9.7 | 8.9 | 6.1
3 | 9.3 | 8.7 | 6.2
4 | 9.5 | 8.5 | 6.2
5 | 9.5 | 8.4 | 6.3
6 | 9.4 | 8.4 | 6.3
7 | 9.2 | 8.3 | 6.2
8 | 9.6 | 8.3 | 5.9
9 | 9.9 | 8.7 | 6.5
10 | 9.7 | 9.8 | 7
11 | 10.6 | 11.6 | 7.3
12 | 10.9 | 13.3 | 7.7
13 | 10.7 | 13.2 | 7.7
14 | 10.9 | 13 | 7.9
15 | 10.7 | 13 | 7.4
16 | 10.6 | 12.1 | 7.9
17 | 10.6 | 11 | 7.6
18 | 10.1 | 10.5 | 7.6
19 | 10.4 | 10.2 | 7.3
20 | 10.6 | 9.9 | 7.3
21 | 9.7 | 9.6 | 6.9
22 | 10.6 | 9.4 | 6.9
23 | 9.6 | 8 | 6.6
0 | 8.5 | 1.9 | 6.3
1 | 7.5 | 4.1 | 5.6
2 | 6.6 | 3.9 | 5
3 | 7 | 3.7 | 5.9
4 | 6.6 | 3.5 | 5.3
5 | 7 | 3.5 | 5.1
6 | 7.3 | 3.4 | 5.3
7 | 6.8 | 3.4 | 4.6
8 | 6.2 | 3.3 | 4
9 | 7.4 | 3.7 | 5.2
10 | 8.6 | 4.8 | 6.4
11 | 9.2 | 6.5 | 8.5
12 | 10 | 8.2 | 9.1
13 | 9.6 | 8 | 9.2
14 | 10.1 | 8.1 | 9.3
15 | 10 | 7.8 | 9.1
16 | 10 | 7 | 8.5
17 | 8.9 | 6 | 7.6
18 | 8.9 | 5.4 | 7
19 | 8.5 | 5.2 | 7
20 | 7.7 | 4.9 | 6.5
21 | 7.7 | 4.6 | 6.4
22 | 8.2 | 4.4 | 6
23 | 6.2 | 3 | 5.7
0 | 3 | 0.7 | 5.4
1 | 3.5 | 2.7 | 5.1
2 | 3.9 | 2.6 | 4.7
3 | 3.7 | 2.4 | 4.3
4 | 3.6 | 2.2 | 5.3
5 | 3.8 | 2.1 | 4.3
6 | 3.8 | 2.1 | 5.2
7 | 4 | 2.1 | 4.5
8 | 3.6 | 2 | 3.7
9 | 4.5 | 2.4 | 5.5
10 | 5.6 | 3.4 | 7.3
11 | 6.2 | 5 | 8.6
12 | 6.7 | 6.6 | 9.7
13 | 6.5 | 6.5 | 9.8
14 | 6.8 | 6.4 | 9.7
15 | 6.6 | 6.1 | 9.5
16 | 6.4 | 5.5 | 9.3
17 | 6 | 4.5 | 8.7
18 | 4.8 | 4 | 7.7
19 | 5.9 | 3.8 | 7.9
20 | 4.7 | 3.5 | 7
21 | 4.4 | 3.2 | 7.1
22 | 4.8 | 3.1 | 5.7
23 | 5.2 | 1.7 | 5.6
0 | 5.6 | 2.6 | 5.5
1 | 6 | 5.5 | 5.2
2 | 6.4 | 5.2 | 5
3 | 6.1 | 5 | 4.8
4 | 6.9 | 4.8 | 4
5 | 6.6 | 4.6 | 4
6 | 6.3 | 4.6 | 3.2
7 | 6 | 4.5 | 2.3
8 | 5.6 | 4.5 | 3.5
9 | 6.3 | 5 | 4.7
10 | 7 | 6.4 | 6.9
11 | 7.8 | 8.6 | 9.2
12 | 8.7 | 10.8 | 10.9
13 | 8.4 | 10.6 | 11.2
14 | 8.7 | 10.4 | 11.3
15 | 8.6 | 10.5 | 11.2
16 | 8.3 | 9.3 | 10.3
17 | 8 | 7.9 | 8.7
18 | 7.3 | 7.2 | 8.1
19 | 7.5 | 6.9 | 7.3
20 | 7.4 | 6.5 | 7.1
21 | 6.9 | 6.1 | 6.2
22 | 6.8 | 5.9 | 6.6
23 | 7.3 | 4.1 | 7.3
0 | 7.8 | 3.4 | 8.1
1 | 8.3 | 5.5 | 9.1
2 | 9 | 5.3 | 9.9
3 | 7.6 | 5.2 | 9.8
4 | 7.7 | 5 | 9.7
5 | 7.4 | 4.9 | 9.5
6 | 7.1 | 4.9 | 9.6
7 | 7.5 | 4.8 | 9
8 | 7.8 | 4.8 | 8.1
9 | 7.8 | 5.1 | 9.9
10 | 9.9 | 6.2 | 11.5
11 | 10.2 | 7.8 | 13.4
12 | 11 | 9.4 | 14.7
13 | 11.1 | 9.3 | 14.7
14 | 11 | 8.9 | 14.8
15 | 10.9 | 9.2 | 14.7
16 | 10.8 | 8.3 | 14.7
17 | 9.3 | 7.3 | 13.2
18 | 10.1 | 6.8 | 12.2
19 | 9.2 | 6.5 | 11.7
20 | 9 | 6.3 | 11.5
21 | 9.1 | 6 | 11
22 | 8.5 | 5.8 | 12.3
23 | 8.6 | 4.5 | 10.8
0 | 8.7 | 2.4 | 9.3
1 | 8.2 | 4.2 | 7.9
2 | 8 | 4.1 | 6.9
3 | 7.9 | 3.9 | 5.8
4 | 7.7 | 3.8 | 6.1
5 | 7.9 | 3.7 | 5.5
6 | 7.7 | 3.7 | 5.1
7 | 7 | 3.6 | 4.8
8 | 6.3 | 3.6 | 5.2
9 | 7.3 | 3.9 | 5.7
10 | 8.4 | 4.8 | 7.3
11 | 10.8 | 6.3 | 8.3
12 | 11.8 | 7.7 | 9.6
13 | 12.2 | 7.6 | 9.9
14 | 12 | 7.3 | 10
15 | 12.1 | 7.2 | 9.6
16 | 11.7 | 6.7 | 8.9
17 | 10.8 | 5.8 | 8.6
18 | 9.9 | 5.4 | 8.4
19 | 9 | 5.2 | 7.4
20 | 9.2 | 4.9 | 7.7
21 | 8.9 | 4.7 | 7
22 | 9.1 | 4.5 | 7.1
23 | 8.1 | 3.3 | 6.2
0 | 7.1 | 1.4 | 5.2
1 | 6.3 | 3.6 | 4
2 | 5.7 | 3.4 | 3.2
3 | 5.2 | 3.2 | 3.1
4 | 4.8 | 3.1 | 2.9
5 | 4.3 | 3 | 2.8
6 | 4.9 | 2.9 | 3
7 | 5.4 | 2.9 | 3.2
8 | 5.1 | 2.9 | 3.5
9 | 5.7 | 3.2 | 2.8
10 | 6.4 | 4.3 | 3.9
11 | 7.7 | 6.1 | 4.6
12 | 8.7 | 7.8 | 4.6
13 | 8.6 | 7.7 | 4.6
14 | 8.9 | 7.6 | 4.6
15 | 8.6 | 7.6 | 4.8
16 | 8.1 | 6.6 | 4.7
17 | 7.8 | 5.5 | 4.5
18 | 6.8 | 5 | 3.8
19 | 7.1 | 4.7 | 3.6
20 | 6 | 4.5 | 3.3
21 | 6.6 | 4.2 | 3.3
22 | 6.7 | 4 | 3.8
23 | 6.3 | 2.6 | 2.8
0 | 5.9 | -0.5 | 0
1 | 6 | 1.9 | 1
2 | 5.8 | 1.7 | 2
3 | 6 | 1.5 | 1.7
4 | 5.5 | 1.3 | 1.4
5 | 6 | 1.2 | 1.2
6 | 5.9 | 1.2 | 1.9
7 | 5.5 | 1.1 | 1.2
8 | 5.4 | 1.1 | 1
9 | 5.2 | 1.5 | 1.9
10 | 6.4 | 2.7 | 3.5
11 | 7.5 | 4.7 | 5
12 | 8.1 | 6.6 | 6.4
13 | 7.9 | 6.4 | 6.4
14 | 8.1 | 6.4 | 6.5
15 | 8.2 | 6.4 | 6.3
16 | 8 | 5.3 | 5.9
17 | 7.1 | 4.1 | 4.4
18 | 6.8 | 3.5 | 4.3
19 | 6.9 | 3.2 | 3.5
20 | 6.5 | 2.9 | 3
21 | 7.3 | 2.5 | 2.9
22 | 6.1 | 2.3 | 3.2
23 | 5.8 | 0.7 | 3.4
0 | 5.4 | 5.5 | 3.7
1 | 4 | 5.9 | 5.2
2 | 3 | 5.9 | 5.9
3 | 3.3 | 5.9 | 5.5
4 | 2.6 | 5.8 | 5.3
5 | 2.3 | 5.8 | 5.7
6 | 2 | 5.8 | 5
7 | 2.4 | 5.8 | 4.2
8 | 2.9 | 5.8 | 3.3
9 | 3.7 | 5.9 | 5.6
10 | 4.4 | 6.1 | 7.7
11 | 6.5 | 6.5 | 9.5
12 | 6.8 | 6.9 | 12
13 | 6.9 | 6.8 | 11.9
14 | 6.7 | 6.4 | 12.1
15 | 7.1 | 6.7 | 12
16 | 6.5 | 6.6 | 11.7
17 | 5.3 | 6.4 | 10.2
18 | 5.7 | 6.2 | 9.2
19 | 5.1 | 6.2 | 8.2
20 | 4.4 | 6.1 | 8.1
21 | 4.6 | 6.1 | 7.8
22 | 4.2 | 6 | 7.4
23 | 4.1 | 5.7 | 9.2
0 | 4 | 5.6 | 11
1 | 3.9 | 7.6 | 11.5
2 | 3.9 | 7.5 | 11.9
3 | 3.5 | 7.3 | 11.7
4 | 2.9 | 7.2 | 12.1
5 | 3.8 | 7.1 | 12.2
6 | 4.5 | 7 | 11.2
7 | 4.4 | 7 | 11.1
8 | 4.4 | 6.9 | 11
9 | 4.4 | 7.3 | 11.5
10 | 5.6 | 8.3 | 12.1
11 | 7.3 | 9.9 | 13.1
12 | 8.2 | 11.5 | 13.9
13 | 8 | 11.4 | 13.8
14 | 8.3 | 11.3 | 14
15 | 8.1 | 11.1 | 13.6
16 | 7.7 | 10.4 | 13.9
17 | 6.5 | 9.4 | 13.6
18 | 6.2 | 8.9 | 13
19 | 6.7 | 8.7 | 12.5
20 | 5.9 | 8.4 | 12.9
21 | 5.6 | 8.1 | 11.8
22 | 4.9 | 8 | 12.2
23 | 4.3 | 6.7 | 11.6
0 | 3.7 | 4.4 | 10.9
1 | 2.6 | 6.6 | 9.1
2 | 2.2 | 6.6 | 9.1
3 | 0.4 | 6.6 | 9.1
4 | 0.8 | 6.4 | 9.2
5 | 0.7 | 6.4 | 9.1
6 | 1 | 6.5 | 9.2
7 | 0.3 | 6.5 | 9.1
8 | -0.2 | 6.4 | 9.1
9 | -0.7 | 6.8 | 9.2
10 | 1.7 | 8 | 9.2
11 | 4.1 | 9.9 | 9.1
12 | 5.9 | 11.4 | 9.1
13 | 5.9 | 11.6 | 9.2
14 | 5.9 | 11.5 | 9.2
15 | 6 | 11.5 | 9.2
16 | 5.6 | 10.4 | 9.1
17 | 4.6 | 9.2 | 9.2
18 | 3.7 | 8.5 | 9.2
19 | 2.4 | 8.1 | 9.1
20 | 2.9 | 7.7 | 9.2
21 | 2.6 | 7.4 | 9.2
22 | 1.3 | 7.2 | 9.2
23 | 1.4 | 5.4 | 9.1
0 | 1.4 | 8.8 | 2.1
1 | 1.4 | 9.8 | 2.9
2 | 1.4 | 9.8 | 3.6
3 | 2.7 | 9.8 | 3.1
4 | 3.8 | 9.7 | 3.5
5 | 3.8 | 9.7 | 3.7
6 | 3 | 9.8 | 4.2
7 | 3 | 9.7 | 3.8
8 | 3.5 | 9.7 | 3.7
9 | 3.8 | 9.9 | 3.7
10 | 5.4 | 10.4 | 5
11 | 8.3 | 11.3 | 6.6
12 | 8.6 | 11.8 | 8
13 | 8.7 | 12.1 | 8
14 | 8.8 | 11.9 | 8.1
15 | 8.7 | 11.7 | 7.7
16 | 8.5 | 11.5 | 8
17 | 6.6 | 11 | 7
18 | 5.8 | 10.7 | 6.1
19 | 5.4 | 10.5 | 5.1
20 | 5.3 | 10.3 | 5
21 | 5 | 10.2 | 4.7
22 | 4.6 | 10.1 | 4.4
23 | 3.8 | 9.2 | 2.1
0 | 3.1 | 6.7 | -3.1
1 | 2.9 | 8.7 | -1.6
2 | 2.6 | 8.7 | -0.2
3 | 2.1 | 8.6 | -1.5
4 | 1.6 | 8.5 | -0.6
5 | 2.4 | 8.5 | -1.1
6 | 3.1 | 8.6 | -1
7 | 2.8 | 8.6 | -0.8
8 | 3.1 | 8.5 | -0.7
9 | 3.1 | 8.8 | -0.6
10 | 3.1 | 9.9 | 0.5
11 | 3.8 | 11.6 | 3.4
12 | 4.6 | 13.1 | 5
13 | 5 | 13.1 | 5
14 | 4.8 | 13.1 | 5.1
15 | 5.1 | 12.9 | 5
16 | 5 | 12 | 4.2
17 | 4.1 | 11 | 2.8
18 | 3.6 | 10.4 | 1.7
19 | 3.2 | 10 | 1.5
20 | 2.9 | 9.7 | 1
21 | 2.7 | 9.4 | -0.1
22 | 2.5 | 9.2 | 0.2
23 | 1.9 | 7.6 | -2.5
0 | 1.4 | 2.5 | -5.2
1 | 0 | 3.2 | -3.6
2 | -1.2 | 3.2 | -2.2
3 | -0.3 | 3.2 | -1.6
4 | -1.4 | 3.1 | -1.9
5 | -1.4 | 3.1 | -2.6
6 | -1.5 | 3.2 | -1.8
7 | -0.4 | 3.1 | -2.2
8 | -1.9 | 3.1 | -2.3
9 | -0.8 | 3.2 | -1.8
10 | 0.7 | 3.6 | 0.8
11 | 4 | 4.2 | 4.3
12 | 6 | 4.6 | 6.8
13 | 6.1 | 4.7 | 6.8
14 | 6 | 4.4 | 6.9
15 | 5.8 | 4.5 | 6.8
16 | 6 | 4.3 | 5.8
17 | 2.9 | 4 | 3.6
18 | 1.9 | 3.8 | 2.5
19 | 2.2 | 3.6 | 2.1
20 | 0.5 | 3.5 | 0.6
21 | 1.1 | 3.4 | 0
22 | -0.5 | 3.4 | -0.7
23 | -0.6 | 2.8 | -0.4
0 | -0.6 | -1.9 | -0.1
1 | 0.8 | 0 | 0.3
2 | 1.9 | 0 | 0.7
3 | 2 | -0.1 | 0.2
4 | 1.9 | -0.2 | 0.1
5 | 1.4 | -0.2 | -0.1
6 | 0.5 | -0.1 | 0
7 | -0.6 | -0.1 | 0
8 | 0.6 | -0.2 | 0.7
9 | 1.6 | 0.1 | 0.1
10 | 2.8 | 1.2 | 1.3
11 | 6.5 | 2.8 | 1.3
12 | 7.2 | 4.4 | 1.4
13 | 7.2 | 4.3 | 1
14 | 7.3 | 4.3 | 1.6
15 | 7.2 | 4 | 1.4
16 | 6.5 | 3.3 | 1.4
17 | 5.5 | 2.2 | 0.8
18 | 4.9 | 1.6 | 0.6
19 | 4.3 | 1.3 | 0.8
20 | 3.3 | 0.9 | 0.3
21 | 3.2 | 0.7 | 1
22 | 1.6 | 0.5 | 0.9
23 | 4.5 | -1.1 | 1
0 | 7.4 | 1.3 | 1.1
1 | 8.1 | 3.8 | 1.9
2 | 8.7 | 3.7 | 2.6
3 | 8.6 | 3.7 | 1.9
4 | 7.9 | 3.5 | 2.4
5 | 7.9 | 3.5 | 2.4
6 | 8.1 | 3.6 | 1.9
7 | 7.8 | 3.6 | 1.9
8 | 7.4 | 3.5 | 2.2
9 | 8.1 | 3.9 | 2.2
10 | 8.6 | 5.2 | 3.1
11 | 10.4 | 7.3 | 4
12 | 10.3 | 9.1 | 4.7
13 | 10.5 | 9.2 | 4.8
14 | 10.4 | 9 | 4.5
15 | 10.3 | 9.1 | 4.5
16 | 10 | 7.9 | 4.4
17 | 9.9 | 6.6 | 3.5
18 | 9.1 | 5.8 | 3.4
19 | 9.1 | 5.4 | 3.4
20 | 9.6 | 4.9 | 2.4
21 | 8.9 | 4.6 | 2.5
22 | 8.1 | 4.4 | 2.3
23 | 8.4 | 2.4 | 2.2
0 | 8.6 | 4.3 | 2.1
1 | 8.6 | 5 | 2.4
2 | 8.7 | 5 | 2.6
3 | 8.5 | 5 | 3.1
4 | 8.4 | 5 | 2.5
5 | 8.5 | 5 | 3.2
6 | 8 | 5 | 2.5
7 | 7.5 | 5 | 2.2
8 | 8.1 | 5 | 1.8
9 | 8.7 | 5.1 | 2.3
10 | 9.1 | 5.5 | 2.7
11 | 10.2 | 6.1 | 4.3
12 | 10.8 | 6.6 | 4.6
13 | 11.1 | 6.7 | 4.5
14 | 11 | 6.6 | 4.9
15 | 10.8 | 6.4 | 4.6
16 | 10.6 | 6.3 | 4.8
17 | 9.8 | 5.9 | 3.6
18 | 9.9 | 5.6 | 3.5
19 | 9.7 | 5.5 | 3.2
20 | 9 | 5.4 | 3.8
21 | 9 | 5.3 | 3.1
22 | 8.7 | 5.2 | 3.4
23 | 8.4 | 4.6 | 3.7
0 | 8 | -2.1 | 3.9
1 | 7.2 | 0.3 | 4.5
2 | 6.7 | 0.3 | 4.8
3 | 6.8 | 0.2 | 5
4 | 6.2 | 0.1 | 5.2
5 | 6.4 | 0.1 | 5.4
6 | 6 | 0.2 | 5.4
7 | 5.4 | 0.2 | 4.6
8 | 4.8 | 0.1 | 3.6
9 | 6.4 | 0.5 | 4.9
10 | 8 | 1.8 | 6.2
11 | 10.3 | 4 | 7.5
12 | 10.9 | 6 | 8.5
13 | 10.8 | 5.9 | 8.4
14 | 11 | 5.7 | 8.6
15 | 10.8 | 5.7 | 8.5
16 | 10.3 | 4.6 | 8.6
17 | 9.1 | 3.2 | 7.1
18 | 7.7 | 2.4 | 6.5
19 | 8.1 | 2 | 6.7
20 | 7.4 | 1.6 | 6
21 | 6.8 | 1.2 | 5.9
22 | 7.1 | 1 | 5.4
23 | 6.9 | -1 | 5.2
0 | 6.7 | -2.8 | 5.1
1 | 7.2 | -0.6 | 5.1
2 | 7.5 | -0.7 | 5.2
3 | 7.5 | -0.7 | 5.4
4 | 7.2 | -0.8 | 4.4
5 | 7.2 | -0.8 | 3.2
6 | 7.2 | -0.8 | 4.2
7 | 6.4 | -0.8 | 5
8 | 5.5 | -0.9 | 4.8
9 | 7.8 | -0.5 | 4.6
10 | 10.1 | 0.7 | 7
11 | 12 | 2.6 | 8.8
12 | 12.7 | 4.1 | 10
13 | 12.8 | 4.3 | 10
14 | 12.7 | 4.3 | 10.1
15 | 12.7 | 4.1 | 10
16 | 11.6 | 3.1 | 9.9
17 | 11 | 1.9 | 7.6
18 | 10 | 1.2 | 7.5
19 | 10.5 | 0.8 | 7.3
20 | 8.8 | 0.4 | 6.2
21 | 8.1 | 0.1 | 6.4
22 | 8.1 | -0.1 | 6.2
23 | 7.6 | -1.9 | 6.8
0 | 7.2 | -1.1 | 7.4
1 | 7.5 | 1.4 | 7.7
2 | 7.6 | 1.4 | 7.6
3 | 7.1 | 1.3 | 7.4
4 | 7.1 | 1.2 | 7.9
5 | 7.7 | 1.2 | 8.4
6 | 7.4 | 1.3 | 9.1
7 | 7.1 | 1.2 | 7.8
8 | 7.3 | 1.1 | 7.8
9 | 7.2 | 1.5 | 9.3
10 | 9 | 2.9 | 9.8
11 | 10.8 | 5 | 10.2
12 | 12.2 | 6.6 | 10.5
13 | 12.3 | 6.9 | 10.4
14 | 12.5 | 6.6 | 10.7
15 | 12.4 | 7 | 10.7
16 | 12.3 | 5.6 | 10.7
17 | 10.3 | 4.2 | 10
18 | 9.9 | 3.5 | 9.4
19 | 9.1 | 3 | 9.2
20 | 9.2 | 2.6 | 9
21 | 7.5 | 2.3 | 8.7
22 | 8.5 | 2 | 8.7
23 | 6.8 | 0 | 8.7
0 | 5.1 | 3.8 | 8.7
1 | 4.8 | 4.8 | 9.2
2 | 4.6 | 4.8 | 9.2
3 | 4.9 | 4.8 | 9.6
4 | 4.9 | 4.7 | 9.3
5 | 5.1 | 4.7 | 8.4
6 | 4.7 | 4.7 | 9.2
7 | 5 | 4.7 | 9.3
8 | 5.4 | 4.7 | 8.7
9 | 5.9 | 4.8 | 7.9
10 | 5.3 | 5.4 | 9.7
11 | 6 | 6.3 | 11.3
12 | 7.2 | 6.8 | 12.5
13 | 7.2 | 7 | 12.5
14 | 7.3 | 6.6 | 12.6
15 | 7.2 | 6.7 | 12.5
16 | 7 | 6.5 | 12.2
17 | 6.7 | 5.9 | 11.2
18 | 6.6 | 5.6 | 11
19 | 6.4 | 5.4 | 10.7
20 | 6.1 | 5.3 | 9.5
21 | 5.7 | 5.1 | 10.2
22 | 5.3 | 5.1 | 9.3
23 | 4.3 | 4.2 | 8.3
0 | -3.6 | 1.4 | 7.3
1 | -2.5 | 3.4 | 4.6
2 | -1.5 | 3.3 | 2.7
3 | -1.3 | 3.3 | 2.2
4 | -2.1 | 3.2 | 1.7
5 | -2.2 | 3.2 | 2.2
6 | -2.3 | 3.3 | 2.8
7 | -1.9 | 3.2 | 2.5
8 | -2.3 | 3.2 | 2.5
9 | -1.3 | 3.5 | 3.4
10 | 0.7 | 4.6 | 3.9
11 | 2.4 | 6.3 | 5
12 | 2.5 | 7.5 | 5.9
13 | 3.1 | 7.8 | 6.4
14 | 3.2 | 7.6 | 6
15 | 3.1 | 7.8 | 6
16 | 2.8 | 6.8 | 6.3
17 | 1.8 | 5.7 | 4.9
18 | 1 | 5.1 | 5.1
19 | 0.3 | 4.7 | 4.2
20 | -0.3 | 4.3 | 4.2
21 | -0.8 | 4.1 | 3.3
22 | -2.3 | 3.9 | 3.7
23 | -1.9 | 2.2 | 3.3
0 | -1.6 | 3.1 | 2.8
1 | -1.2 | 4.1 | 3
2 | -0.9 | 4.1 | 3.4
3 | -0.2 | 4 | 3.9
4 | -1.4 | 4 | 2.9
5 | -2.8 | 4 | 2.3
6 | -1.6 | 4 | 3.5
7 | -0.5 | 4 | 2.7
8 | -0.5 | 4 | 1.9
9 | -0.2 | 4.1 | 3.1
10 | 1.4 | 4.7 | 4.4
11 | 3.7 | 5.6 | 6
12 | 4.9 | 6.2 | 6.8
13 | 4.9 | 6.3 | 6.9
14 | 5 | 6 | 6.8
15 | 4.9 | 5.9 | 6.7
16 | 4.3 | 5.8 | 6.4
17 | 3.2 | 5.2 | 5.3
18 | 2 | 4.9 | 4.7
19 | 1.4 | 4.7 | 4.7
20 | 1 | 4.6 | 5
21 | 0.2 | 4.4 | 3.9
22 | 0.3 | 4.3 | 3
23 | 0.8 | 3.5 | 3.4
0 | 1.3 | 2.5 | 3.9
1 | 1.3 | 3.6 | 3.9
2 | 1.3 | 3.6 | 3.7
3 | 1.9 | 3.6 | 4
4 | 2.2 | 3.5 | 3.7
5 | 2 | 3.5 | 3.3
6 | 2.4 | 3.5 | 3.7
7 | 2.6 | 3.5 | 3.9
8 | 3.5 | 3.5 | 4.7
9 | 2.2 | 3.7 | 4.5
10 | 3.3 | 4.2 | 5
11 | 3.9 | 5.2 | 5.9
12 | 5.1 | 5.6 | 6
13 | 5 | 6 | 6.2
14 | 5.1 | 5.9 | 6
15 | 4.9 | 6 | 6.1
16 | 4.5 | 5.4 | 6.1
17 | 4.3 | 4.8 | 5.8
18 | 3.5 | 4.5 | 5
19 | 2.6 | 4.3 | 5.1
20 | 3.3 | 4.1 | 5
21 | 2.3 | 4 | 3.6
22 | 3.5 | 3.9 | 3.9
23 | 3 | 3 | 4.2
0 | 2.5 | 3.5 | 4.5
1 | 1.8 | 5.4 | 4.8
2 | 1.3 | 5.4 | 5
3 | 1.4 | 5.4 | 4.6
4 | 1.1 | 5.3 | 5.2
5 | 0.7 | 5.3 | 4.5
6 | 0.8 | 5.3 | 3.7
7 | 0.9 | 5.3 | 4.1
8 | 1 | 5.2 | 4.4
9 | 2 | 5.5 | 4.8
10 | 2.2 | 6.6 | 4.8
11 | 3 | 8.2 | 7.2
12 | 3.5 | 9.5 | 7.4
13 | 3.6 | 9.7 | 7.2
14 | 3.5 | 9.4 | 7.6
15 | 3.5 | 9.4 | 7.5
16 | 3.5 | 8.7 | 7.3
17 | 2.9 | 7.6 | 6.5
18 | 3 | 7 | 6.1
19 | 2.1 | 6.7 | 5.7
20 | 1.9 | 6.4 | 5.7
21 | 1.7 | 6.1 | 5.4
22 | 1.5 | 5.9 | 6.1
23 | 3.4 | 4.4 | 3.7
0 | 5.3 | 3.5 | 0.2
1 | 5.6 | 5.5 | 0.7
2 | 6 | 5.5 | 1.1
3 | 5.4 | 5.4 | 1.1
4 | 5.6 | 5.3 | 1.8
5 | 6 | 5.3 | 1.1
6 | 6.3 | 5.4 | 1.9
7 | 5.5 | 5.4 | 1.7
8 | 5.5 | 5.3 | 0.8
9 | 5.7 | 5.6 | 1.5
10 | 5.6 | 6.7 | 2.9
11 | 7.6 | 8.5 | 3.8
12 | 7.7 | 9.8 | 4.9
13 | 7.7 | 10.1 | 4.9
14 | 7.8 | 10.1 | 4.6
15 | 7.5 | 9.9 | 4.9
16 | 7.8 | 9 | 4.8
17 | 7.1 | 7.9 | 4.4
18 | 7.4 | 7.2 | 3.1
19 | 6.3 | 6.8 | 3.2
20 | 7 | 6.5 | 2.1
21 | 7.4 | 6.2 | 2.1
22 | 5.5 | 6 | 1.9
23 | 5.4 | 4.4 | 0.9

## References
References
[1] | Department for Environment Food & Rural Affairs (DEFRA). (2018). Milk availability, usage and production - dataset. Retrieved from https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/738409/milkutil-dataset-06sep18.ods
[2] | Ramírez, C. A., Patel, M., & Blok, K. (2006). From fluid milk to milk powder: Energy use and energy efficiency in the European dairy industry. Energy, 31(12), 1648–1668. http://doi.org/10.1016/j.energy.2005.10.014
[3] | Tuszyński, W. B., Diakowska, E. A. A., & Hall, N. S. (1983). Energy in established milk collection and processing. In Solar energy in small-scale milk collection and processing. FAO. Retrieved from http://www.fao.org/docrep/003/X6541E/X6541E02.htm
[4] | The Carbon Trust. (2010). Industrial Energy Efficiency Accelerator. Guide to the dairy sector. Retrieved from https://www.carbontrust.com/media/206472/ctg033-dairy-industrial-energy-efficiency.pdf
[5] | Xu, T., & Flapper, J. (2011). Reduce energy use and greenhouse gas emissions from global dairy processing facilities. Energy Policy, 39(1), 234–247. https://doi.org/10.1016/j.enpol.2010.09.037
[6] | Griffin, P., Hammond, G. P., & Norman, J. B. (2013). Industrial Energy Use from a Bottom-Up Perspective: Developing the Usable Energy Database. London, UK: UKERC.
[7] | Eames, M., Kershaw, T., & Coley, D. (2011). On the creation of future probabilistic design weather years from UKCP09. Building Services Engineering Research and Technology, 32(2), 127–142. https://doi.org/10.1177/0143624410379934
[8] | BEIS. (2017). Greenhouse gas reporting: conversion factors 2017. Retrieved from https://www.gov.uk/government/publications/greenhouse-gas-reporting-conversion-factors-2017
[9] | BEIS. (2018). Updated energy and emissions projections: 2017. Retrieved from https://www.gov.uk/government/publications/updated-energy-and-emissions-projections-2017
[10] | J. Jutsen, A. Pears, and L. Hutton, “High temperature heat pumps for the Australian food industry: Opportunities assessment,” Sydney, 2017.
[11] | M. Nilsson, H. N. Rislå, and K. Kontomaris, “Performance testing of a lab-scale high temperature heat pump with HFO-1336mzz-Z as the working fluid,” in 12th IEA Heat Pump Conference 2017, 2017.
[12] | EHPA, “NeatPump,” 2015. [Online]. Available: https://www.ehpa.org/about/news/article/the-worlds-largest-natural-district-heat-pump/. [Accessed: 05-Aug-2018].
[13] | Cooper, S. J. G. (2013). Thermodynamic Analysis of Air Source Heat Pumps & Micro Combined Heat & Power Units Participating in a Distributed Energy Future. University of Bath, Thesis (PhD). Retrieved from opus.bath.ac.uk
[14] | TetraPak. (2018). Dairy Processing Handbook. Retrieved September 2, 2018, from http://dairyprocessinghandbook.com/chapter/heat-exchangers